JASPERS

Joint Assistance to Support Projects in European Regions

Sectoral EIA Guidelines

Bulgaria

Waste Water Treatment Plants and Waste Water Collection Systems

FINAL DRAFT

2013

Preface

The purpose of these Guidelines are primarily aimed at EIA practitioners in Bulgarian environmental authorities/competent authorities and could be used also by the consultants for developing sound EIA Reports for projects in those sectors more frequently requesting Community financial support.

It is envisaged to outline issues, which may be relevant for the evaluation of the environmental impact assessment report for water and waste water infrastructure projects. It could be also of importance for other authorities that must be consulted in accordance with the legal provisions, for the non-governmental organizations as well as the public and to facilitate their enhanced participation in the EIA process. The contained recommendations will be hopefully of practical benefit to those involved in the EIA process for water and waste water infrastructure projects.

Table of Contents

1	Introduction	8

2	Policy, legal and administrative framework	9

3	Description of the proposed project	11

3.1	Description of location and land use requirements	11

3.2	Description of the Project design	12

3.3	Description of the main processes	15

3.4	Estimation of residues and emissions resulting from the implementation of the project	16

4	An outline of the main alternatives studied by the developer	18

4.1	Main alternatives studied by developer	18

4.2	Baseline scenario	19

4.3	Alternative selection	19

5	Description of the existing environment (baseline conditions)	21

5.1	Context	21

5.2	Character	21

5.2.1	Water and Groundwater	22

5.2.2	Soil and Geology	23

5.2.3	Air and climate	23

5.2.4	Human beings	23

5.2.5	Fauna and flora	24

5.2.6	Landscape	24

5.2.7	Material assets	24

5.2.8	Cultural heritage	25

5.3	Significance	25

5.4	Sensitivity	25

5.5	Sufficiency of data	25

6	Description of the likely significant environmental impacts and mitigation measures	26

6.1	Prediction of the likely significant impacts	26

6.2	Description of the likely significant environmental effects and  their mitigation	27

6.2.1	Water and groundwater	27

6.2.2	Soil and geology	31

6.2.3	Air and climate	33

6.2.4	Human beings	35

6.2.5	Fauna and flora	37

6.2.6	Landscape	39

6.2.7	Material assets	40

6.2.8	Cultural heritage	41

6.3	Residual impact assessment	42

6.4	Cumulative impact assessment	42

6.5	Risks cases	43

7	Environmental Monitoring Programme	45

8	Non-technical summary	51

9	Challenges in EIA Report preparation	52

10	Environmental Management Plan	53

11	References	55

Annexes	56

# Acronyms

| BOD | Biochemical oxygen demand |
| --- | --- |
| CA | Compatibility Assessment |
| CoM | Council of Ministers |
| CJEU | Court of Justice of the European Union |
| COD | Chemical oxygen demand |
| DWTP | Drinking water treatment plant |
| ExEA | Executive Environment Agency |
| EA | Environmental Assessment |
| EIA | Environmental impact assessment |
| EIAD | EIA Directive |
| ELW | European Waste List |
| EMP | Environmental Management Plan |
| EU | European Union |
| LBD | Law on Biological Diversity |
| LEP | Law on Environmental Protection |
| LW | Law on Waters |
| MoEW | Ministry of Environment and Water |
| MS | Member state |
| NTS | Non-technical Summary |
| p.e. | Population equivalent |
| RBMP | River Basin Management Plan |
| RIEW | Regional Inspectorate of Environment and Water |
| SEA | Strategic Environmental Assessment |
| SG | State Gazette |
| TDS | Total dissolved solids |
| TKN | Total Kjeldahl Nitrogen |
| TSS | Total suspended solids |
| WFD | Water Framework Directive |
| WPS | Water pumping station |
| WSS | Water supply system |
| WWCS | Waste water collecting system |
| WWPS | Waste water pumping station |
| WWTP | Waste water treatment plant |

# Foreword

These Guidelines were prepared as part of a standard set of tools to be used by beneficiaries, project developers and environmental authorities in any interested EU Member State and were then adapted to Bulgarian national requirements, for developing and reviewing sound EIA Reports for projects in those sectors more frequently requesting EU financial support. It is also envisaged for other authorities that must be consulted in the EIA process in accordance with the relevant procedural and legal provisions and for consultants assigned to prepare EIA Reports.

The Guidelines aims at ensuring that those responsible for carrying out the assessment and preparing the EIA Report are fully aware of the relevant issues and will address them adequately. If efficiently used, the tool will help to improve the quality of the EIA Reports and ultimately facilitate their review and the approval process for EU funding.

These Guidelines shall apply to the following types of projects as listed in Annex I and Annex II of the EIA Directive (2011/92/EU), respectively under the Law on Environmental Protection (LEP), as listed in Table 1.

Table 1 Projects to which these guidelines are applicable respectively under Annex I and II of the EIA Directive and Annex I and II of the LEP

| Annex I and II of the EIA Directive | LEP |
| --- | --- |
| Annex I(13) – “Waste water treatment plants with a capacity exceeding 150000 population equivalent as defined in point 6 of Article 2 of Council Directive 91/271/EEC of 21 May 1991 concerning urban waste-water treatment;” | Annex I, point 28 of the LEP - Wastewater treatment plants with a capacity exceeding 150,000 population equivalent |
| Annex I(24) – “Any change to or extension of projects listed in this Annex where such a change or extension in itself meets the thresholds, if any, set out in this Annex.” | Annex I, point 38 of the LEP - Any change to or extension of a development proposal included in this Annex, where such a change or extension in itself meets the thresholds, if any, set out in this Annex |
| Annex II(10)(b) – “Urban development projects, including the construction of shopping centres and car parks ; | Annex II, point 10(b) of the LEP - urban development projects, including the construction of shopping centres and car parks |
| Annex II(11)(c) – “Waste water treatment plants (projects not included in Annex I) ”; | Annex II (11) (c) of the LEP - waste-water treatment plants (not included in Annex 1); |
| Annex II(13)(a) – “Any change or extension of projects listed in Annex I or this Annex, already authorised, executed or in the process of being executed, which may have significant adverse effects on the environment (change or extension not included in Annex I).” | Article 93(1)(3) of the LEP - any extension or modification of development proposals according to Annex 1 hereto and Appendix I to Article 2 of the Convention on Environmental Impact Assessment in a Transboundary Context, which have already been approved or are in the process of being approved, have been executed or are in the process of being executed, provided any such extension and/or modification may cause a significant adverse impact on the environment |

While defining the scope of the projects covered by these Guidelines, it should be stressed again that in the “Interpretation of definitions of certain project categories of annex I and II of the EIA Directive” the EC has interpreted the issue related to the consctruction of sewerage and water supply networks as projects falling under the scope of EIA Directive, namely as infrastructure projects for urban development under Annex II(10)(b).

The structure of the Guidelines follows to a large extent the requirements provided in Annex IV of the EIA Directive with respect to the information referred to in Article 5(1) of the EIAD, respectively in Article 96(1) of the LEP and Article 12 of the Ordinance on the conditions and the order for implementing environmental impact assessment (EIA Ordinance), i.e. the information that the developer has to provide to the competent authority or authorities for projects that are subject to an EIA.

The Guidelines address the project types mention above, as defined in the EIA Directive (Annexes I and II), respectively in Annexes I and II of the LEP, in a single document and comments on those issues which may be specific to one type or another as appropriate. However, the recommendations are not exhaustive and some issues common to all type of projects may not be covered.

The final environmental impact assesment report is referred to as EIA Report. Most national environmental legislations specify what the content of EIA Report should be, as is the case under Bulgarian national legislation. The sections of this document provide recommendations for a standard structure of the EIA Report and for the issues that shall be addressed/covered under each of the respective sections and sub-sections.

The sections of these Guidelines will follow a possible content of an EIA Report, which largely follows the requirements of the LEP and the EIA Ordinance:

- Introduction

- Policy, legal and administrative framework

- Description of the proposed project

- Outline of the main alternatives

- Description of the environment

- Description of likely significant environmental impacts and mitigation measures

- Monitoring Program

- Non-Technical Summary

- Challenges in EIA Report preparation

- Environmental Management Plan

- List of References

The proposed order and scope is not mandatory or exhaustive but should be adapted according to the characteristics of the individual project. This relates to the Project objectives, technical characteristics, location, natural and built environment and other elements.

As long as the proposed order and scope is not mandatory or exhaustive, it should rather be adapted as appropriate according to the requirements of the LEP and the EIA Ordinance.

It should be noted again that the EIA Report may make use of this structure, but should consider complying with the requirements of Article 96(1) of the LEP and Article 12 of the EIA Ordinance. More specifically, Article 96(1) of the LEP makes the following mandatory to the content of the EIA report:

“1. a summary of the development proposal for execution of construction, activities and technologies;

2. (amended, SG No. 77/2005) alternatives of siting (including plats and bearings of typical points within the established national coordinate system) and/or alternatives to the technologies as studied by the initiator and reasoning of the choice of study made, considering the environmental impact, including a "zero alternative";

3. a description and analysis of the environmental media and factors covered under Articles 4 and 5 herein and of the physical structures and the cultural heritage that will be significantly affected by the development proposal, as well as the interaction among these aspects;

4. description, analysis and assessment of the potential significant effects on the population and the environment resulting from:

(a) implementation of the development proposal;

(b) use of natural resources;

(c) emissions of harmful substances in normal circumstances and in an emergency, generation of waste and creation of nuisances;

5. information on the forecasting methods used to assess the effects on the environment;

6. a description of the measures envisaged to avoid, reduce and, if possible, remedy significant adverse effects on the environment, as well as a plan for implementation of the said measures;

7. (supplemented, SG No. 46/2010, effective 18.06.2010) observations and opinions expressed by the public concerned, of the authorities competent to make an EIA decision or officials empowered thereby and other specialized institutions and the States affected in a transboundary context, as a result of the consultations held;

8. (amended, SG No. 77/2005, SG No. 103/2009) conclusion in conformity with the requirements of Article 83 (5) herein;

9. a non-technical summary of the information;

10. information on the difficulties (technical reasons, insufficiency or lack of data) encountered in the collection of information for preparation of the EIA statement;

11. (supplemented, SG No. 46/2010, effective 18.06.2010) other information at the discretion of the competent authority or an official empowered thereby.”

This legal framework is supplemented by Article 12 of the EIA Ordinance, as following:

“(1) The EIA report shall be formed as an integral document, which includes:

1. a main content part in accordance with Article 11(1);

2. list of the sources of information used by the authors in the EIA report;

3. the summarized reference under Article 9(5);

4. (new, SG 29/2010) list of the experts and the team leader, who have prepared the EIA report, where each one signs under the sections of the report, prepared by him/her;

5. (new, SG 29/2010) written declarations under Article 11(3) signed personally by the experts;

(2) As separate self-standing annexes to the EIA report are enclosed:

[…]

4. the assessment under Article 99a(1) of the LEP for the cases under Article 118(2) of the LEP for each of the installation, falling under the scope of Annex IV of the LEP;

5. a non-technical summary of the EIA report under Article 96(1)(9) of the LEP

6. (new, SG 3/2011) the assessment of the extent of the impact in the cases where the competent authority has required the preparation of such.“

Note that these Guidelines do not attempt to reproduce any statutory EIA guidelines that already exist in the member states and should always be read in conjunction with the EU Directive on EIA and Bulgarian national legislation and guidance on EIA, as detailed legal requirements vary throughout the country.

# Introduction

Usually the EIA Report structure follows the sequence of the information as required by Article 5(3), and which is detailed in the Annex IV of the EIA Directive, as implemented by Article 96(1) of the LEP and Article 12 of the EIA Ordinance. In addition, the EIA Report should contain:

- the name and qualifications of the specialists who prepared each section, the submission date, the signature of the responsible person / official representative of the firm that prepared the EIA Report;

- an overview of the policy, legal and administrative framework governing the EIA and waste water treatment sector;

- an overview of the steps of the EIA procedure carried out up to EIA Report completion;

- the description of how were considered, during the EIA Report preparation:

  - the outcomes of the consultations of the authorities likely to be concerned by the project by reason of their specific environmental responsibilities and,

  - the outcomes of the public consultations;

- appendices containing:

  - drawings, maps, diagrams, etc.;

  - documents, studies, and information used as reference for the EIA Report preparation;

  - copies of certain documents, which are relevant for the EIA carried out for the Project;

- a Glossary of terms and acronyms.

The introductory section of the EIA Report should provide a concise presentation of how is set out the content of the EIA Report, and information regarding the EIA procedure carried out for the Project.

- Information recommended to be presented in the introductory section of an EIA Report

Project title

Project developer

Needs and specific objective(s) of the proposed project

Description of the EIA Report content

Estimated life time of the Project and if the case and Project components

Implementation schedule / project phasing Starting and finishing dates for construction; in the case of staged projects, the order of each stage and its approximate duration Commissioning date Starting and finishing dates demolition activities, in the case of such activities are required

Data about sequence of the EIA procedure stages accomplished so far for the project; name the documents provided by competent authority provided during EIA procedure, if applicable (e.g. screening decision, scoping report)

Outcomes of the consultation of other authorities likely to be to be concerned by the project by the reason of their environmental authorities and, if applicable, name of the documents issued by other authorities and specification of the appendix of the EIA Report where they can be find

Outcomes of the consultation of the public concerned about the project

# Policy, legal and administrative framework

The objective of this section of the EIA Report is to provide an overview of the national environmental policy and the national and EU legislation that has been taken into consideration in carrying out the EIA.

This chapter considers the relevance of European and national legislation, national planning, policy, and the compatibility of the project with this legislation/policy. It highlights and addresses the policies of national government ministries, where relevant, and outlines those EU directives and regulations and other international obligations that are applicable to the project.

## EU legislation relevant for the project

Article 11 of the Treaty on the Functioning of the European Union (TFEU) proclaims the principle of integration of the environmental considerations into the other sectoral policies, in particular with a view to promoting sustainable development.

Article 191 of the TFEU states that EU environmental policy must contribute to preservation, protection and improvement of the quality of the environment, protection of human health, to prudent and rational utilisation of natural resources, and should aim at a high level of protection of the environment. The EU environmental policy is based on the precautionary principle, ‘and on the principles that preventive action should be taken, that environmental damage should as a priority be rectified at source and that the polluter should pay.’

The relevant EU legislation includes directives applicable specifically to urban waste water treatment, water quality and those requiring assessments of impact of the specific projects on the environment:

- Directive 2011/92/EU of the European Parliament and of the Council of 13 December 2011 on the assessment of the effects of certain public and private projects on the environment

- Council Directive 91/271/EEC of 21 May 1991 concerning urban waste water treatment, as amended

- Directive 2000/60/EC of the European Parliament and of the Council of 23 October 2000 establishing a framework for Community action in the field of water policy, as amended

Other EU environmental legislation may also be relevant, which includes Directive 2001/42/EC on the assessment of the effects of certain plans and programmes on the environment and Directive 92/43/EEC on the conservation of natural habitats and of wild fauna and flora, as amended and Directive 2009/147/EC on the conservation of wild birds.

EU environmental acquis on air quality, waste management, access to environmental information, etc. may be applicable to the individual project phases: construction, exploitation, decommissioning and should also be taken into consideration.

In addition, the EU legislation regulating, for example, energy efficiency of buildings, occupational safety and health may also be relevant.

In compliance with provisions of the Treaty of the European Union and Treaty on the Functioning of the European Union, these directives are transposed into national law and thus do not need to be considered in more details, instead, the national legislation transposing them must be presented.

Last but not least, the case-law developed by the Court of Justice of the European Union (CJEU) must be taken into account. Although the jurisprudence of the Court does not require transposition, the interpretation therein is mandatory for the Member States and the EU institutions.

## Bulgarian legislation relevant for the project

The applicable national legislation is presented in Box 2 below.

- Applicable legislation

Spatial Planning Legislation

Law on Spatial Development: Regulates the social relations associated with spatial development, development-project designing and construction in the Republic of Bulgaria and determines the restrictions on ownership for spatial-development purposes. Relevant is the procedure of issuing a construction permit, which under the said Law goes roughly through the following steps: Step 1: (when necessary and if not developed so far development of development schemes and plans Pursuant to Article 125(1) and (6) of that Law, draft spatial-development plans shall be prepared on the basis of terms of reference including, where necessary, a basic plan, as well as from additional information relating to the spatial development of the relevant spatial-development area, provided by the municipalities, the Geodesy, Cartography, and Cadastre Agency, the central and local administrations and corporations which shall prepare selective maps, registers and information systems. These ToR are submitted to the Ministry of Environment and Water or to the competent Regional Inspectorate of Environment and Water for determination of the need of an environmental impact assessment according to a procedure established by the ordinance referred to in Article 90 of the Law on Environmental Protection. The environmental impact assessment shall be part of the spatial-development plan. Step 2: issuing of design visa Step 3: preparation of an investment project Step 4: coordination of the project with the utility companies (electricity, water and heat supply, etc.) Step 5: assessment of the compatibility of the project with the detailed spatial plan Article 144(1) reads that any development-project designs, which serve as grounds for the issuance of a building permit, shall be approved acting on a written application by the contracting authority and after submission of the, inter alia, administrative acts which, depending on the type and size of the construction work, are required as a condition for permission of construction under the Environmental Protection Act or a special law. Step 6: approval of the project by the expert council Step 7: issuance of the construction permit Article 148(8) states that the approved development-project design, where such shall be required, shall constitute an integral part of the building permit. Any effective EIA decision or decision exempting from the EIA requirement as provided for in the Law Environmental Protection constitutes an appendix to and an integral of the building permit.

Environmental policy and legislation framework

The protection of the environment is a right and obligation of the State and all citizens in compliance with Constitution of the Republic of Bulgaria: “The Republic of Bulgaria shall ensure the protection and reproduction of the environment, the conservation of living Nature in all its variety, and the sensible utilization of the country's natural and other resources.” Again, according to the Constitution, all Bulgarian citizens are entitled to have a healthy and favourable environment corresponding to established standards and norms and are obliged to protect the environment. The Law on Environmental Protection (LEP) provides for the overall legal framework for protection of the environment. This framework is supplemented by a number of other primary and secondary legislation acts regulating the management of the different components and factors of the environment. Under Article 2 the objectives of the Law are the following: “1. regulating of the regimes for preservation and use of the components of the environment; 2. control over the status and the use of the components of the environment and sources for its pollution and damaging; 3. establishing of admissible standards for emissions and for quality of the environment; 4. management of the components and the factors of the environment; 5. implementing of environmental impact assessment (EIA); 6. issuing of permissions for prevention, restriction and control of the pollution; 7. announcing and management of territories with special regime of protection; 8. development of the system of monitoring of the components of the environment; 9. introduction of economic regulators and financial mechanisms for management of the environment; 10. regulation of the right and the obligations of the state, the municipalities, the corporate bodies and the individuals.” In compliance with the Law, the environmental protection is based on the principles for sustainable development, prevention and reduction of the risk for human health, priority of prevention of pollution over follow-up removal of the damages, public participation and transparency in the process of environmental decision-making; access to information in environmental matters, polluter pays, preservation, development and protection of the ecosystems and their intrinsic biological diversity, restoration and improvement of the quality of environment in the polluted and damaged regions, prevention of pollution and damaging of the clean regions and other unfavourable impacts on them, integration of the environmental protection policy in the sectoral and the regional policies for development of economy and public relations and access to justice. The state environmental protection policy is integrated in the following sector policies: transport, power generation, construction, agriculture, tourism, industry, education, etc. The competent authorities and their responsibilities are defined in Article 10 of the LEP: “(1) Competent authorities under this Act shall be: 1. the Minister of Environment and Water; 2. the executive director of the Executive Agency for Environment; 3. the directors of the Regional inspectorates for environment and water (RIEW); 4. the directors of the basin directorates; 5. the mayors of the municipalities, and in the towns with district division – also the mayors of the districts; 6. the regional governors.

(2) Competent to undertake the actions and activities, provided in the law, shall be: 1. on the territory of one municipality – the director of RIEW 2. on the territory of one region – the regional governor or the director of RIEW; 3. on the territory of several municipalities within the scope of one RIEW – the director of the respective inspectorate; 4. on the territory of several municipalities within the scope of different RIEW – the Minister of Environment and Water.” The Minister of Environment is responsible inter alia for: development of environmental protection policy and the strategy in the Republic of Bulgaria; managing through the Executive Environment Agency the National System for Monitoring of Environment; control the status of environment on the territory of the country; coordination of the control authorities of the other authorities of the executive power with regard to the environment; In coordination with other state authorities the Minister: issue standards for maximum admissible emissions from types of pollutants and standards for maximum admissible concentrations of harmful substances for components of the environment in regions; approve methods for EIA; issue standards for rational use of renewable and not renewable natural resources; The National Environmental Protection Strategy 2000-2006 sets as a long-term objective the improvement of the quality of life through the maintenance of favourable environment and reservation of the rich nature based on the sustainable development of the environment. This overall objective is supplemented by sectoral objectives covering water and air quality, nature protection, waste management, etc. The National Action Programme for Environment and Health 2008-2013 aims at: further improvement of the conditions for coordination and cooperation in the implementation of the national policy in compliance with the National Health Strategy and the National Environmental Protection Strategy at national, regional and local level. issuing orders, permits, instructions and approve methodologies, etc. ensure the collecting and the conceding of information about the status of the environment; approve methods for control of the components of the environment. strengthening and improvement of the inter-sectoral cooperation in the implementation of the environmental and health protection policy, while environmental and health protection become a main principle of development programmes in all economic sectors; In view of achieving these general objectives, the Programme provides for specific measures with a timetable, competent authority and financial resources for their implementation.

Legislation on EIA

EIA is regulated by the: Law on Environmental Protection; Ordinance on the conditions and the order for implementing environmental impact assessment Pursuant to the Law on Environmental Protection, the EIA determines, describes and assesses in appropriate way for each individual case the direct and the indirect impacts of the investment proposals for construction, activities and technologies over humans, biological diversity and its elements, including flora and fauna, the soil, the water, the air, the climate and the landscape, the earth bowels, the material and the cultural–historic heritage and the interaction between them. EIA is mandatory for all investment proposals included in Annex I of the LEP. Annex I, point 28 refers to: Annex I, point 28 of the LEP - Wastewater treatment plants with a capacity exceeding 150,000 population equivalent In cases of changes and extensions of the investment proposals under point 28, where this change or extension individually meets the criteria, if any, indicated in this Annex, EIA is also compulsory. The LEP provides for an EIA screening for all Annex II projects, which also include in point 11(c) waste-water treatment plants (not included in Annex 1); and any extension or change of such investment proposals, which have already been approved or are under a process of approval, have been accomplished or are in a process of implementation, if this extension or change may result in a significant impact of the environment. It should be noted that point 10 of the Annex II of the LEP (and of the EIA Directive) refers to “infrastructure” investment proposals. In the Guidance on the Interpretation of definitions of certain project categories of Annex I and II of the EIA Directive, the European Commission takes the view that: “The term ‘infrastructure’ is widely interpreted and may include roads, power, and other utility services provided to facilitate the growth of industries.”

Hence, and in view of the broad purpose and wide scope of the EIA legislation also other water and waste water infrastructure investment proposals may require an EIA. In addition to the above and in compliance with the interpretation of the EIA Directive by the Court of Justice of EU (CJEU) and the European Commission, the obligation for carrying out an EIA is also extended to construction of sewerage and water supply networks which are covered by Annex II(10)(b) of the EIA Directive (and also by point 10(b) of Annex II to the LEP). Also the relevant case-law developed by the CJEU should be considered and more specifically that all activities, including the supporting and auxiliary ones, should be assessed together. Competent authorities for EIA are the Minister of Environment and Water and the Director of the respective RIEW, as defined in Article 94(1) and (2) of the LEP. The Ordinance on the conditions and the order for implementing environmental impact assessment supplements the provisions of the LEP and provides for the detailed rules for EIA, including preparation of the EIA report, holding consultations with the other authorities and the public and transboundary consultations, decision-making and control for compliance with the EIA decision conditions.

Water Quality Policy and Legislation

National Environmental Protection Strategy 2000-2006 The National Environmental Protection Strategy sets as specific objectives for the water sector: to ensure water supply for the population and the economy of the country; to overcome the critical water supply problems; to provide for water for irrigation; to create awareness and interest for economized use of water resources; to preserve and improve the quality of ground- and surface waters. National Strategy on the Management and Development of the Water Sector in the Republic of Bulgaria The National Strategy on the Management and Development of the Water Sector in the Republic of Bulgaria was adopted by a National Assembly Decision of 21 November 2012 (promulgated SG 97 of 7 December 2012) and aims at implementing and supplementing the National Environmental Protection Strategy. The main objective of the Strategy is sustainable development of the water resources, ensuring optimal level of the present and future needs of the population and the economy of the country and of the water eco-systems. The Strategy has the following three objectives supporting the achievement of the main one: Objective 1: to ensure the water supply for the population and the economy of the country in a situation of changing climate conditions leading to more scarce water resources; Objective 2: preservation and improvement of the surface and groundwater status; Objective 3: improvement of the efficiency of the integrated management of water as an economic resource. The Law on Environmental Protection and the Law on Waters (LW) are the main legislative acts that regulate water management in Bulgaria, by providing for the basic principles of effective environmental policy, such as ‘polluter pays’, ‘public awareness regarding the state of the environment’, ‘shared responsibility’, ‘preventive action (and control)’, ‘integrated management’. Law on Environmental Protection Article 35 of the LEP states as a general principle that the preservation and the use of waters and water bodies is based on a long-term state policy, on the rational management of the waters at national and basin level so that good status of all the waters is achieved. The preservation of the waters and the water bodies must ensure: the balance between the exploitation of the waters and their natural restoration; the preservation and the improvement of the surface and the groundwater.

Law on Waters The LW regulates the ownership and management of waters in Bulgaria as a national integral natural resource and the ownership of water economic systems and facilities. This framework is supplemented by the Law on State Property and the Law on Municipal Property. The requirements of the WFD are transposed into the national law, including those on the establishment and the application of the river basin management principle. Water management is carried out at national level and at river basin level. According to the LW, water management includes the activities for water use, protection and restoration as well as the activities for prevention of the harmful impact of waters. Bulgarian water management policy at national level is implemented by the MoEW, which is responsible for the management of water resources and their distribution among the consumers. Permitting regime is provided for water intake and use of water bodies, while the latter includes the discharge of waste waters to into surface waters. More specifically, such permit is issued for: design of facilities, including sewage systems for settlements and resorts and for design of an extension or modification of existing facilities, when it leads to changes of the parameters and the point of the permitted discharge; exploitation of existing facilities, including sewage systems for settlements and resorts. The water discharge permit is a legally based pre-condition for the commissioning of urban waste water treatment plants (UWWTPs). At the same time, in compliance with the LEP and the Law on Biological Diversity (LBD), respectively the positive EIA decision or the negative screening decision, the positive compatibility assessment decision or the decision stating that such an assessment is not necessary, are pre-requisites for granting the water discharge permit. The detailed terms and the procedure for issuing the permit are provided in Ordinance No. 2 of 8 June 2011 on the issuing of permits for the discharge of waste waters in water bodies and setting individual emission restrictions to point pollution sources (please see below). Pursuant to the LW, the Minister of Environment and Water is the competent authority responsible also for the following main areas: development of the national water management policy, as well as the drafting of national legislation in the area of water protection, including pollution by urban waste water; proposes to the Council of Ministers the approval of river basin management plans; issuing permits for water use and permits for discharge of treated waste water into dams covered by Annex I of the LW; preparation of annual report on the environmental situation, including water, with the aim of providing information to the public, etc. The river basins are the basic units for the integrated water management. There are four river basin districts in the country, which are designated according to the natural situation of watersheds dividing the drainage areas of one or several major rivers within the territory of the country. For these four districts River Basin Management Directorates are established within the structure of the MoEW as the bodies implementing the water management policy at local level. The River Basin Management Directorates perform the following main functions: organizing the preparation of river basin management plans and conducting public discussion of these plans; issuing permits for water use and permits for discharge and all permits under the LW, not falling under the competences of the Minister or another authority; jointly with the municipalities defining the boundaries of waters and water bodies, constituting public state property; issuing permits for discharge of waste water, keeping of registers and controlling the observance of the terms and requirements of the issued permits; maintaining the National System for Water Monitoring at basin level; organizing and managing the collection and control of the results from the internal monitoring of the enterprises; issuing opinions on the admissibility of investment proposals for their compliance with the river basin management plan and plan on the management of flood risk; updating the control information system for the condition of the waste water; developing proposals for improvement, protection and maintenance of good water conditions, etc. The River Basin Management Directorates participate in the regional, municipal and district spatial development councils. They prepare and present written opinions on investment projects for development, reconstruction or rehabilitation of the water supply and sewage networks and systems, including treatment plants for drinking and waste water. The Regional Inspectorates on Environment and Water (RIEW) under the MoEW ensure the state environmental policy at regional level and perform: monitoring of waste waters; controls the sources of waste waters, including the UWWTPs, the parameters and compliance with the requirements under the permits for waste water discharge and the integrated permits under the LEP; control the emergency releases of waste water; maintain a database on the monitoring and control concerning the condition of waste water. The Executive Environmental Agency under the MoEW performs: monitoring and controls quality of water by physical and chemical parameters through mobile laboratories; water monitoring at national level; maintains geographic information system for the waters at national level; prepares an annual report on the water status; issues a periodical bulletin on water status creates and maintains specialized data bases, maps, registers and a water information system. Briefly, pursuant to the LW, the responsibilities of the remaining competent authorities are as follows: Ministry of Regional Development and Public Works is responsible for the water supply and sewerage systems and facilities in settlements and for protection against water-related damage and loss within the limits of settlements; the Minister of Regional development and Public Works exercises the rights of state ownership in the water companies wherein the state is the sole owner or holds a share of the capital exceeding 50%; Ministry of Agriculture and Food is responsible for irrigation and land-reclamation systems and facilities and for protection against water-related damage and loss beyond the boundaries of settlements; Ministry of Economy, Energy and Tourism is responsible for hydro-energy systems and facilities; Ministry of Health is responsible for the exercise of monitoring and control on the quality of surface water intended for drinking and household use, as well as of bathing water. The commercial water supply and sewage companies (WSSC) operate the facilities. The municipal administrations play an important role in the implementation of the environmental policy in the water sector. Their main tasks include: construction, maintenance and proper operation of the sewage networks and the facilities for UWWTPs; the construction and registration of small facilities for individual water use from the ground waters on the territory of the municipality. The WSSC are responsible for the activities related to the operation and maintenance of water supply facilities (at the sources of drinking water, drinking water treatment plants, pumping stations, water reservoirs and water supply network) and the sewerage networks (for waste water collection, treatment and discharge). The LW envisages the planning of the development of the water supply and sewage (WSS) to be made by WSS regional master plans and WSS master plans for agglomerations with above 10 000 p.e. These plans are adopted for a period of 25 years and cover the following analysis of the state and the necessities of the WSS systems and facilities of the respective territory; analysis of the price and the quality of the WSS services provided in the separated territory as well as a development prognosis for the WSS service in view of achieving users’ satisfaction, water loss reduction and guaranteeing good quality of the service at a socially acceptable price objectives and priorities for development of WSS systems and facilities in the individual territory so that compliance with EU law and with the programmes of measures related to collection, discharge and treatment of waste waters from urbanized territories as provided in the respective river basin management plan is achieved; a long-term investment programme for the implementation of the plan and a short-term investment programme for the first five-year period. These master plans are to be prepared by the WSSC or the by the respective municipal councils. Before being adopted these plans should be made subject to environmental assessment and must be endorsed by the respective river basin directorates and municipal councils. Currently these master plans are under preparation for adoption. All four river basin management plans have been adopted and are currently implemented. For the purposes of implementation of Directive 91/271/EEC, National programme for priority construction of urban waste water treatment plants was developed by the MoEW in 1999, which aims at setting priorities for construction of UWWTPs at watersheds for all settlements with more than 10000 p.e. This programme was supplemented by the adopted in 2003 National Programme of the Implementation of Directive 91/271/EEC. The legislation in the country also introduces economic instruments, which regulate and guide the behaviour of the water users and the condition of the water bodies. The requirements to UWWT are mainly regulated by Ordinance No. 6 of 9 November 2000 on the emission values of admissible content of harmful and dangerous substances in waste waters discharged in water bodies and Ordinance No. 2 of 8 June 2011 on the issuing of permits for the discharge of waste waters in water bodies and setting individual emission restrictions to point pollution sources. Bulgaria has negotiated the following transitional periods for the implementation of UWWT Directive: ‘By way of derogation from Articles 3, 4 and 5(2) of Directive 91/271/EEC, the requirements for collecting systems and treatment of urban waste water shall not fully apply in Bulgaria until 31 December 2014, in accordance with the following intermediate target: by 31 December 2010, compliance with the Directive shall be achieved in agglomerations with a population equivalent of more than 10 000.’ Ordinance No. 6 of 9 November 2000 on the emission values of admissible content of harmful and dangerous substances in waste water discharged in water bodies Ordinance No. 6 aims at reduction of the harmful and dangerous substances released with the waste waters. This Ordinance sets the emission values of admissible content of harmful and dangerous substances in waste waters discharged in water bodies. The individual emission restrictions provided for in the discharge permits cannot be less strict than those given in the Ordinance. In cases of transboundary waters subject to international conventions or agreements, in the permits the stricter emission values apply. All discharges of waste waters in groundwater fall under the scope of Ordinance No. 6. Hence, it provides for emission values for discharges from certain industrial activities and after urban waste water treatment. Ordinance No. 6 also provides provisions for monitoring for compliance with the requirements therein. In accordance with this Ordinance, all agglomerations above 2000 p.e. must construct centralized sewage network for collection and direction of waste waters for biological treatment. The sewage system may be designed as such for joint acceptance of domestic, industrial and rainwater or for acceptance of domestic and industrial or for domestic waste waters only. The necessary biological treatment may be ensured by the construction of one or more UWWTPs or of an UWWTP that serves more than one agglomeration. It is also possible that the system is connected to an existing plant. In compliance with the negotiated transitional periods, the following deadlines for construction of sewage systems and installations for treatment are envisaged: for agglomerations with above 10000 p.e.: 31/12/2010; for agglomerations between 2000 and 10000 p.e.: 31/12/2014. Pursuant to Table 1 of Annex III of Ordinance No. 6 waste waters from UWWTPs should comply with the following: Parameter Concentration Biological Oxygen Demand (BOD5) and 20°С without nitrification 25 mg/dm3 O2 Chemical Oxygen Demand (COD) 125 mg/dm3 O2 Total suspended solids 35 mg/dm3 (optional) 35 mg/dm3 under Article 11(2) (more than 10 000 p.e.) 60 mg/dm3 under Article 11(2) (2 000-10 000 p.e.) For all agglomerations above 10000 p.e. which discharge waste waters in a water body defined as a sensitive area, in addition to the biological treatment, also removal of the nitrogen and phosphorus is required within the allowed concentrations. Pursuant to Table 2 of Annex III of Ordinance No. 6 the following requirements for removal of the nitrogen and phosphorus to waste waters from UWWTPs discharging in sensitive areas apply: Parameter* Concentration Total nitrogen 15 mg/dm3 for 10 000 - 100 000 p.e. 10 mg/dm3 for above 100 000 p.e. Total phosphorus 2 mg/dm3 for 10 000 - 100 000 p.e. 1 mg/dm3 for above 100 000 p.e. * One or both parameters apply depending on the actual situation. Annex IV to this Ordinance provides for the criteria for designation of sensitive areas. The list of the sensitive areas was adopted in 2003 and it defined as sensitive areas the Danube River and the Black Seas their catchment areas, parts of the rivers Struma, Arda, Maritza and Tundzha. Ordinance No. 2 of 8 June 2011 on the issuing of permits for the discharge of waste waters in water bodies and setting individual emission restrictions to point pollution sources The objective of Ordinance No. 2 is to provide for conditions for reduction of water pollution and protection of surface waters quality where waste waters are discharged. The Ordinance defines the terms and the procedure for issuing permits under Article 46(1)(3) of the LW for use of water body for discharge of waste waters into surface waters, the so called ‘discharge permits’. It also defines the requirements to the determination of the individual emission restrictions for point sources in accordance with Article 120 of the LW. Discharge permits under Ordinance No. 2 are issued for the following: design of facilities, including of sewage systems for settlements and resorts exploitation of existing facilities, including sewage systems for settlements and resorts These permits may be for grouped collection and directing, treatment and discharge of waste waters by two or more plants. Ordinance No. 7 of 14 November 2000 on the terms and procedure for discharge of industrial waste waters in the settlements sewerage systems Ordinance No. 7 aims at protection of water bodies used for discharge of waste waters from pollution with toxic, harmful and dangerous substances. The Ordinance regulates the rights and the obligations of the legal and natural persons generating industrial waste waters and the operators of sewage systems which make part of the contracts for use of these systems for discharge of such waters. The operators of sewage systems may impose individual emission restrictions to the content of polluting substances. Other secondary legislation on water quality in Bulgaria includes: Ordinance No. 1 on exploration, use and protection of groundwater (SG 87 of 30/10/2007, as last amended and supplemented SG 28 of 19/03/2013) Ordinance No. 3 of 16/10/2000 on the conditions and the procedure for exploration, design and exploitation of sanitary-protection zones around the water sources and facilities and around the mineral water sources used for health treatment, prophylactics, drinking and hygiene needs (SG 88 of 27/10/2000) Ordinance No. 5 of 30/05/2008 on the management of bathing waters quality (SG 53 of 10/06/2008, as last amended and supplemented SG 5 of 18/01/2013) Ordinance No. 4 of 20/10/2000 on the quality of water intended for fishery and breeding of shellfish organisms (SG 88 of 27/10/2000) Ordinance No. 18 of 27/05/2009 on the quality of waters used for irrigation for agricultural products (SG 43 of 09/06/2009) Ordinance No. 1 on monitoring of waters (SG 34 of 29/04/2011, as amended and supplemented SG 22 of 05/03/2013) Ordinance No. 12 on the requirements to the quality of surface waters intended for drinking and human consumption supply (SG 63 of 28/06/2002, as amended SG 15 of 21/02/2012) Ordinance No. N-4 of 14/09/2012 on the characterization of surface waters (SG 22 of 05/03/2013) Ordinance No. 2 of 13/09/2007 for protection of waters with nitrates from agricultural sources (SG 27 of 11/03/2008, as amended and supplemented SG 97 of 09/12/2011)

Waste Management Legislation

The National Waste Management Programme 2009-2013 covers all waste streams and aims at ensuring full compliance with the existing waste management legislation. The Law on Waste Management is the main legal instrument in the sector. It lays down measures and control mechanisms to protect the environment and human health by preventing or reducing the adverse impacts of the generation and management of waste and by reducing overall impacts of resource use and improving the efficiency of such use. To that end, it establishes the requirements to products which, in the process of production thereof or after final use thereof, generate hazardous and/or ordinary waste, as well as the requirements for extended producer responsibility relating to such products so as to promote the re-use, prevention, recycling and other recovery of waste. The following ordinances may be relevant to the project: Ordinance No. 3 on the classification of waste Ordinance No. 2 of 22/01/2013 on the procedure and the templates for submission of information on the activities with waste, as well as the procedure for maintaining the public registries Ordinance on the management of construction waste and for the application of recycled construction materials Ordinance No. 6 of 28/07/2004 on the conditions and the requirements for the construction and exploitation of the installations for incineration and of installations for co-incineration of waste Ordinance on the requirements to treatment and transport of industrial and hazardous waste Ordinance on the procedure and the methods for recovery of sewage sludge from treatment of waste waters by using it in the agriculture Ordinance on the waste oils and waste petrol products

Air quality

Legislation defining and setting up objectives for ambient air quality, legislation related to the limitation of emissions of flue gases and permissible emission levels from different types of vehicles, Legislation establishing methods and criteria for the monitoring of air quality and modelling methodologies for air pollutant dispersion. The framework on air quality in Bulgaria is regulated by the Law on Clean Ambient Air and a number of secondary legislation acts. The objective of Law is to protect the people's and their generation's health, the animals and the plants, their communities and habitats, the natural and cultural values from harmful effects, as well as to prevent the occurrence of dangers and damages to society in case of changes in the ambient air quality resulting from various activities.

The Law regulates: the specification of indices and standards of ambient air quality; the limitation of emissions; the rights and obligations of the state and municipal authorities, of the legal and natural persons as regards the control, management and maintenance of the ambient air quality. the requirements for the quality of liquid fuels, including the control of compliance with the requirements for liquid fuel quality at the time of their placing on the market and their distribution, transportation and use. the limitations on the emissions of sulphur dioxide from the use of liquid fuels, the limitations on the sulphur content of oil derivatives and the method of their combustion by vessels staying in the ports of the Republic of Bulgaria, the Bulgarian section of the Danube river, the inland sea waters, the territorial sea and the exclusive economic zone. The requirements of the Law apply to: sites and facilities intended for production and non-production purposes which are being designed, built and operated; means of transport and other individual sources of pollution; construction and other open sites; construction, destruction, extraction, transport, communal, agricultural and other activities; tanks for storage and use of liquid fuels, petrol facilities, terminals, gasoline stations, road and railway tankers, ship fuel tanks, with the exception of motor vehicle fuel tanks. The following ordinances may apply to the project: Ordinance No. 12 of 15/07/2010 on the norms for sulphur dioxide, nitrogene, particulate matter, lead, benzene, carbon dioxide and ozone in the ambient air Ordinance No. 11 of 14/05/2007 on the norm for arsenium, cadmium, nickel and polycyclic aromatic carbon oxides in the ambient air Ordinance No. 1 of 27/06/2005 on limit emission values for harmful substances (pollutants) released in the atmosphere by installations and activities with immovable sources of emissions Ordinance No. 6 on the procedure and the methods for measurement of emission of harmful substances released in the ambient air by immovable sources of emissions Ordinance No. 10 of 24/02/2004 on the conditions and the procedure for approval of the types of internal combustion engines to be installed off-road mobile machinery regarding their emissions of pollutants Ordinance No. 7 on the assessment and management of the quality of ambient air Ordinance No. 14 on the norms for limit admissible concentrations of harmful substances in the ambient air of the settlements Ordinance on the requirements to the quality of liquid fuels, the conditions, the procedure and the methods for controlling them

Noise

Legislation related to noise levels for outdoor used equipment, from different types of vehicles, assessment and modelling methodologies. The Law on Protection Against Environmental Noise sets out the legal framework for management of environmental noise. The objective of the Law is to establish healthy living conditions and for protection of the environment from noise shall be achieved by development and implementation of an integrated approach and measures for noise avoidance, prevention or reduction. The Law regulates: the assessment, management and control of environmental noise emitted by road, railway, air and water traffic, as well as by industrial installations and facilities, including the categories of industrial activities referred to in Appendix No. 4 to Article 117, Para. 1 of the Environmental Protection Act , and by local noise sources; the determination of the degree of environmental noise by measurement, assessment and mapping of environmental noise levels and by strategic noise mapping; the acoustical planning by development of action plans based upon noise-mapping results, with a view to preventing and reducing environmental noise, particularly where exposure levels can induce harmful effects on human health, and to preserving environmental noise quality where it is good; the access to and provision of information to the public on environmental noise and its effects; the competencies of the governmental authorities and the local government authorities, the rights and obligations of legal entities and sole proprietors involved in the assessment, management and control of environmental noise. The legal framework is supplemented by the: Ordinance No. 54 of 13/12/2010 on the activities of the national system for monitoring of the environmental noise and the requirements to self-monitoring and submission of information by the industrial sources of environmental noise Ordinance No. 6 of 26/06/2006 on the indicators for environmental noise, measuring the level of discomfort during the different parts of the day, the limit values of the indicators for environmental noise, the methods for assessment of the limit values of the indicators for noise and the harmful effects of the noise on the health of the population Ordinance No. 3 on the requirements to the establishment, maintenance and the content of the registries of the agglomerations, main roads, railways and airport in the country Ordinance on the requirement to the development and the content of the strategic noise maps and to the action plans Ordinance to the essential requirements and to the assessment of the compliance of outdoor machinery and equipment regarding the noise emitted by them in the air

Soil

The Law on Soils regulates the social relations in connection with the protection of soils and their functions, as well as their sustainable use and long-term restoration as an environmental medium. Soils are defined as a national asset and a scarce, irreplaceable and essentially non-renewable natural resource, and their protection is a priority and obligation of state and municipal authorities and of natural and legal persons. Soil protection, use and restoration shall be based on the following principles: an ecosystem and comprehensive approach; sustainable use of soils; a priority of preventive control to forestall or limit soil degradation and damage to soil functions; applying good practices in soil use; the polluter pays for the damage caused; public awareness of the environmental and economic benefits of soil protection from degradation and of measures to preserve soils. The objective of the Law is to ensure: prevention of soil degradation and damage to soil functions; lasting protection of soil functions; restoration of damaged soil functions. In addition the following soil legislation may by applicable: Ordinance No. 3 of 01/08/2008 on the norms for admissible content of dangerous substances in the soils Ordinance No. 4 of 12/01/2009 on the soils monitoring Ordinance No. 26 of 02/10/1996 on the rehabilitation of damaged terrains, improvement of low-productive lands, reclamation and recovery of humus layer Ordinance on the inventory and exploration of the terrains with polluted soils, the necessary remediation measures, as well as the maintenance of the implementation of the remediation measures Ordinance on the procedure and the methods for inventory, exploration, implementation and maintenance of the necessary remediation measures on terrains with damaged soils Ordinance No. 36 of 18/08/2002 on the conditions and the procedure for biological testing, registration, use and control of fertilizers, soil improvers, biologically active substances and food substrates

Flora, fauna and natural habitats

The legislation relevant to water and waste water infrastructure projects, and in particular when it is likely that there will be adverse effects on NATURA 2000 sites and when compatibility assessment will be required: Law on Biological Diversity (LBD) Ordinance on the conditions and order for carrying out compatibility assessment on plans, programmes, projects and investment proposals with the conservation objectives of the protected areas (CA Ordinance) The Law on Biological Diversity provides for the establishment of the National Ecological Network of protected areas, designated in compliance with the EU Habitats and the Birds directives, which are now part of the European NATURA 2000 Network. The protection regime under Article 6(3) and (4) of the Habitats Directive is laid down in Article 31-34a of the said law. Hence, compatibility assessment is required for all plans, programmes, investment proposals and projects not directly connected or necessary for the management of the protected area which individually or in combination with other plans, programmes and investment proposals are likely to have significant adverse effect on the site. The compatibility assessment aims at assessing these effects against the subject of protection and site-specific protection objectives. The LBD provides for joint procedures when compatibility and environmental or environmental impact assessments are required simultaneously. When the plan, programme or investment proposal is not covered by the LEP and relevant secondary legislation adopted there in, the compatibility assessment is implemented in compliance with the LBD and the CA Ordinance. Pursuant to the LBD, plans, programmes, projects or investment proposals are only approved if the compatibility assessment reaches the conclusion that the subject of protection of the site would not be significantly adversely affected. If, however, the plan, programme, project or investment proposal needs to be approved for a reason of an overriding public interest and no other alternative exists, then compensatory measures must be implemented and the procedure for communication with the European Commission must be complied with. The Ordinance on the conditions and order for carrying out compatibility assessment on plans, programmes, projects and investment proposals with the conservation objectives of the protected areas (hereafter the CA Ordinance) supplements the provisions of the LBD and provides for the detailed procedure for the implementation of the compatibility assessment. The competent authorities for the compatibility assessment are the Minister of Environment and Water and the director of the respective RIEW. More specifically, the Minister is competent for: the plans, programmes and investment proposals and their modifications and extensions not covered by the LEP and implemented on the territory of more than one RIEW; for the plans, programmes and investment proposals and their modifications and extensions not covered by the LEP and implemented in the territory of a protected area under the Law on Protected Areas and for the plans, programmes or other projects approved or adopted by the central authorities of the executive power and the National Assembly;

The director of the respective RIEW is the competent authority for all other the plans, programmes, projects and investment proposals. In the cases when the compatibility assessment is combined with an environmental or an environmental impact assessment the competences of the authorities are defined under the respective provisions of the LEP and the relevant secondary legislation adopted therein (as described above). In addition, the following legal acts may be applicable: Ordinance on the development of management plans for protected areas Ordinance No. 2 of 18/12/2006 on the conditions and the procedure for the establishment and the functioning of the National System for Monitoring of the Status of the Biological Diversity Ordinance No. 5 of 01/08/2003 on the conditions and the procedure for preparation of action plans for plant and animal species Decision No. 122 of the Council of Ministers (CoM) of 02/03/2007 for the adoption of a List of Protected Areas for Protection of Wild Birds and a List of Protected Areas for Protection of Natural Habitats and Wild Flora and Fauna Decision No. 661 of the CoM of 16/10/2007 for the adoption of a List of Protected Areas for Protection of Natural Habitats and Wild Flora and Fauna Decision No. 802 of the CoM of 04/12/2007 for the adoption of a List of Protected Areas for Protection of Wild Birds and a List of Protected Areas for Protection of Natural Habitats and Wild Flora and Fauna

Health and safety legislation

The Law on Health regulates the social relations concerning the protection of the citizens' health. The protection of the citizens' health as a condition of full physical, mental and social wellbeing is a national priority and it shall be guaranteed by the government through the application of the following principles: equality in the use of health services; ensuring accessible and high-quality healthcare, giving priority to children, pregnant women and mothers of children aged up to one year; priority of health promotion and the integrated disease prevention; prevention and reduction of the health risk to citizens as a result of adverse effects of environmental factors; special health protection of children, pregnant women, mothers of children aged up to one year and people with physical and mental disabilities; participation of the government in the financing of activities aimed at protecting the health of citizens.

The Law on Health and Safety Labour Conditions regulates rights and duties of the state, employers, employees, persons, who alone or in cooperation with other persons work for their own, other organizations and legal persons in respect of the provision of healthy and safe working conditions. Bulgarian Secondary legislation may include: Ordinance No. 3 of 28/02/1987 on the mandatory preliminary and periodic medical checks of workers Ordinance No. 3 of 19/04/2001 on the minimum requirements for the safety and protection of the health of the workers when using personal protection means at their working place Ordinance No. 7 of 23/09/1999 on the minimum requirements to the health and safety labour conditions at the working places and when working equipment is used Ordinance No. 3 of 25/01/2008 on the conditions and the procedure for the operation of the services for occupational medicine Ordinance No. 3 of 27/07/1998 on the functions and the tasks of the officials of the specialized services in the enterprises for organization of the implementation of the activities related to protection against professional risks and prevention of such risks Ordinance No. 15 of 31/05/1999 on the conditions, procedure and requirements to development and introduction of physiological regimes of labour and rest during work time

Access to environmental information

The requirements related to access to environmental information are provided in the LEP and the Law on Access to Public Information.

Cultural heritage

The Law on Cultural Heritage regulates the preservation and protection of the cultural heritage of the Republic of Bulgaria regardless of its location. The cultural heritage includes the non-tangible and tangible immovable and movable heritage as an aggregate of cultural values which bear the historical memory and national identity, and have scientific or cultural importance. The Law establishes a system for protection of the immovable cultural heritage, namely pursuant to Article 83-85 of the Law Cultural Heritage and Article 56(4), Article 57(5), Article 62(8), Article 125(5), Article 140(3), Article 141(7), Article 143 (1)(5), Article 147(3), Article 148(8), Article 151(2), Article 169(3)(1), Article 224(1)(6) and Article 225(2)(5) of the Law on Spatial Development, a procedure for authorization by the Minister of Culture of investment projects and of rquests for interventions in protected areas for protection of the cultural heritage is established. The compliance with this procedure is a pre-requisite for lawful construction.

# Description of the proposed project

This section of an EIA Report should contain such information and level of detail as to provide reviewers, decision makers and concerned and interested parties with a complete overview of relevant features throughout all phases of the Project from its design through to its physical existence and operation. Typically, this section of an EIA Report will comprise of 4 sub-sections, namely

- Description of location and land use requirements

- Description of design

- Description of the main processes;

- Estimation of residues and emissions resulting from the implementation of the project.

It is important to note that this section will only cover the selected alternative, while earlier considered options are presented in a separate section of the EIA Report. The following subsections mainly address the construction of a new WWTP and water supply network/WWCS; however, the same principal structure should be followed in case where an existing water or waste water infrastructure is to be extended or rehabilitated.

## Description of location and land use requirements

The description should include information about the project location (and in particular, the locations of the project components including, such as buildings or other physical structures, pipelines, etc.), and the vicinities of the project area. It should also contain similar information in relation with the construction phase of the project and the components of the project (construction yard, work sites).

- Data regarding project location and land use requirements

Agglomeration

Description of the agglomeration location;

Localities within the agglomeration;

Administrative area covered by the agglomeration.

Water Supply System

Description of the WSS location;

Localities within the WSS;

Administrative area covered by the WSS.

Water supply network and WWCS

Location of the of the works envisaged by the project:

water supply network: main water transmission, drinking water treatment plant, reservoirs, water pumping station, networks etc.;

WWCS: WWPS(s), storm overflow basins, main collectors, waste water networks;

information regarding the area where the proposed water supply infrastructure is proposed to be developed: the land area; the size of area required for the main components of the water supply infrastructure; the land use in the vicinity of the works (agricultural, residential, commercial, recreation, industrial areas, tourist areas, institutions, etc.); distances from project location(s) to those areas.

WWTP

Location of the WWTP;

Land area required for the WWTP;

Size of the area required for the main components of the WWTP;

Vicinities of the WWTP: land use (agricultural, residential, commercial, recreation, industrial areas, tourist areas, institutions); distances of project location(s) to these areas.

Construction yard, work sites

Land use of the proposed area of the construction yard and work sites; the extent of work sites;

Design limitations imposed by the site characteristics (including adjacent land use);

Locations of the work sites in relation with the works envisaged by the project: if the locations have not established yet, the EIA Report should contain proposals for those work sites. The proposals will be done considering the size and the type of the works envisaged by the project;

Vicinities of the work sites locations: land use (agricultural, residential, commercial, recreation, industrial areas, tourist areas, institutions); distances from the project/project component location to those areas.

Design limitations imposed by site characteristics

Land use of the site of the project/project component location;

Adjacent land use.

## Description of the Project design

The design of projects concerning water supply infrastructure and waste water infrastructure, including waste water treatment, should ensure the compliance with the existing legislation, in the context of the following EU directives:

- Council Directive 98/83/EC on the quality of water intended for human consumption;

- Directive 2000/60/EC establishing a framework for Community action in the field of water policy;

- Council Directive 91/271/EEC concerning urban waste water treatment.

Furthermore, the project design should also take into account the requirements to the quality of the ground water and surface water, as defined by the River Basin Management Plan (RBMP) covering the water bodies where the project is planned to be located.

- Content of a RBMP

A RBMP sets the measures, which are envisaged as necessary to the achievement of the objectives of the WFD. The river basin management plan for each river basin district should include the following: General description of the characteristics of the river basin district, including a map showing the location and boundaries of the surface and ground water bodies and a further map showing the types of surface water bodies within the basin; Summary of the significant pressures and the impact of anthropogenic activity on the status of surface and ground waters, including point source pollution, diffuse pollution and related land use, the quantitative status of water including abstractions and an analysis of other impacts of human activity on water status; Map showing any protected areas; Map of the monitoring network; Map of the results of the monitoring programme showing the status of all water bodies and protected areas; List of the environmental objectives set for all water bodies, including those where the use has been made of derogations; Summary of the economic analysis of water use; Summary of the programme or programmes of measures; Register of any more detailed programmes and management plans and a summary of their contents; Summary of the public information and the consultation measures taken, their results and the changes to the plan as a consequence; List of competent authorities; Contact points and procedures for obtaining background documentation and information, including actual monitoring data. (Foundation for Water Research http://www.euwfd.com/html/development_of_river_basin_management_plans.html)

The key issues regarding the project componenets that the EIA Report should include are presented in Box 5.

- Data regarding project design

Agglomeration

The designed capacity of the agglomeration - BOD load of the waste water generated by the agglomeration expressed (p.e) considering decrease/increase load in the future;

Anticipation of future BOD load will take into consideration the development of the areas from the urban development point of view, and the possible changes of industrial discharges (reduction or increase of flows and specific pollutants);

Where two or more individual agglomerations can be joined together in such way as the waste water collected to be treated in a single WWTP, the data will be provided for each agglomeration, and for the group of agglomerations.

WWTP

Flows: dry weather flow and rain flow;

Waste water balance for the proposed WWTP: domestic, industrial and non-domestic and run-off (m³/day, m³/year);

Urban waste water treatment process:

pre-treatment: screening, grit removal;

primary treatment: sludge settling and grease removal;

secondary treatment: waste water biological treatment and secondary sedimentation;

tertiary treatment: nitrogen and phosphorus removal and additionally, if it is required by local conditions, disinfection.

The design of the waste water treatment will consider, depending on the anticipated loading, the way of integrating septic into the treatment process.

Sludge treatment:

Works/equipment for sludge treatment;

Treatment process: thickening, anaerobic stabilisation (digestion), dewatering, filters, centrifugation;

Sludge quantity resulted from the waste water treatment; humidity (dry matter);

Storage facilities for the sludge; the design of the storage facilities should consider the option for the final waste destination: use it agriculture, landfill or incineration.

WWCS

Localities covered by the WWCS and afferent inhabitants;

Data about storm overflow basins (if applicable), main collectors, WWPSs, networks;

Percentage of population connected to WWCS.

Water Supply System

Localities covered by the WSS and afferent inhabitants;

Specific water consumption: domestic water demand (house connection, yard connection, public tap supplies) and non-domestic water demand: specific flow - corresponding to the specific type of industry;

Percentage of population connected to WSS.

Main water transmission and drinking water supply network, waste water collectors, waste water network:

Route, pipeline material, length, diameters, flows, pressure.

To facilitate a good understanding of the project, the description of project location and description of design should be accompanied by maps, diagram etc., which are significant from the environmental protection point of view:

  - map showing the proposal in the regional context;

  - map showing administrative borders of localities included in the agglomeration, agglomerations borders, WSS, borders, and the locations of the main project works (including water and waste water networks);

  - maps showing the existing land use in the area of the project/project component, and in the area of the construction yard and work sites;

  - process flow diagram for the waste water treatment;

  - process flow diagram for the sludge treatment.

If a project concerns the rehabilitation/extension of existing infrastructure, additional information must be provided, depending on the relevant project characteristics.

Some examples are given in Box 6.

- Information regarding existing water supply and/or waste water infrastructure in project area

Agglomerations

Agglomeration/s, boundaries of the agglomeration/s;

COD load of the waste water generated by the agglomeration/s expressed in p.e.;

Data related to the existing WWCS;

Physical condition of the infrastructure, including references to the civil structures.

WWCS

Type (unitar y system/separate system);

Data regarding storm overflow structures, if applicable (size, location etc.);

Network (e.g. length, materials, diameters, routes etc.)

WWPS (shape, capacity, location etc.).

WWTP

Description of the WWTP components, e.g.: inlet pumping station, pre-treatment, primary sedimentation, biological treatment, secondary clarifier, sludge treatment, other components, such as treated waste water outlet pipeline;

Evaluation of the waste water and sludge treatment performance.

Water supply infrastructure

Localities areas covered by WSS and afferent inhabitants;

Raw water sources;

Works: transmission main, DWPS, reservoirs, drinking water network, etc. ( e.g. chlorination station);

Localities served by an existing WSS, specific water consumption, connection rate.

Physical condition of water and/or waste water infrastructure

Pipes;

Civil structures;

Installations – e.g. pumping installation

Main deficiencies identified

Main deficiencies of the WWCS and WWTP, e.g. waste water loss (networks, main collectors), reduced efficiency of the WWTP, high energy consumption, inadequate management of the waste generated by the WWTP and collecting system operation, particularly the sludge resulted from the WWTP operation, etc.;

Main deficiencies of the water supply network, e.g. limited supply area, non-compliance with water and health regulations on drinking water quality, water loss (water supply and drinking water distribution network, water main transmission), frequent interruptions in drinking water supply, low coverage of drinking water demand, high energy consumption, accidents risk through chlorine equipment (such as obsolete dosing devices), etc.

## Description of the main processes

The activities during the construction phase of the project, concern arrangements for a construction yard, working site preparation, construction activities and, if the case, decommissioning or demolition activities. The description of activities related to the operation phase should address issues about the operation and maintenance of the project components. Box 7 provides an overview of the issues to be addressed in the EIA Report in relation to the project activities.

- Project activities

CONSTRUCTION

Construction yard preparation

Removal of the vegetation from the construction yard area;

Topsoil removal and storage, excavations/ backfilling works, transport and disposal of surplus excavated material; flattening of construction yard location;

Accommodation facilities for the construction yard: water supply (domestic and technological if any), discharge of waste water and installations for treatment and/or removal of liquid effluents, where appropriate, electric supply, waste disposal etc.;

Storage facilities for the building materials;

Parking and maintenance of the equipment used for construction activities;

Fencing of construction yard;

Access roads

Decommissioning or demolition activities

Types of the works (civil structures, concrete sewer pipes, asbestos pipes etc.);

Decommissioning/demolition methods;

Main equipment used;

On-site temporary waste storage facilities.

Construction activities

Sequence of the activities, taking into account the type of works in project area and different type of construction activities (excavations, civil works, pipes lay down etc.);

Infrastructure diversions (temporary and/or permanent);

Equipment, heavy machinery and vehicles, and construction procedures to be used;

Installation of the equipment (for WWTP, WPS, etc.);

Foresseble characteristics of the works in terms of workforce and sites;

Works for the protection of archaeological sites, historical monuments, or relevant material assets (if applicable).

OPERATION

WWTP

Technological operations required for the WWTP operation;

Quality control - the efficiency of the waste water and sludge treatment processes;

Maintenance operations;

Technological operations required for the sludge facilities operation;

Transport, storage and handling of the wastes resulted from WWTP operation.

WWCS

Maintenance operations of the sewage network (pipelines, WWPS, storm overflow basins, etc.);

Transport, storage and handling of the waste resulted from maintenance operations;

On-site inspection activities: pipes integrity, civil structures;

Water supply network

On-site inspection activities: equipment, pipes integrity, civil structures;

Maintenance activities - equipment of the water supply network (e.g. pumping stations).

Drawings and flow diagrams

WWTP facilities and afferent waste water treatment process;

Sludge treatment facilities and afferent treatment process.

For the above presented activities, the materials intended to be used (including those that may be harmful to the human health or for the environment) information should be presented, both for the construction and operation phase of the project.

The following issues regarding the materials intended to be used should also be addressed:

- materials: types and quantities;

- storage facilities;

- storage locations;

- handling conditions.

## Estimation of residues and emissions resulting from the implementation of the project

Estimation of the residues and emissions should be done considering the project components, equipment and construction techniques, respectively the specific operation activities, and corresponding materials, which are intended to be used.

- Estimation of residues and emissions

CONSTRUCTION

Emissions

Liquid effluents: sources, characteristics (estimated composition, flows/quantities);

Gas emissions: sources, characteristics (estimated composition, flows/quantities);

Dust emissions: sources, characteristics (estimated composition, flows/quantities);

Noise generation (sources and intensity in decibels) and vibration.

Waste

Types of waste, e.g.: materials resulted from excavation/ dredging not being used for backfilling, humus layer, contaminated soils or other materials, household non-hazardous waste, hazardous waste, waste resulting from construction or demolition activities, pipes, equipment resulting from dismantling/decommissioning operations; sludge resulted from the operation of WWTP (in the case of rehabilitation of an existing WWTP).

Waste classification (estimated composition, hazardous properties, ELW codes)

Estimated quantities of each type of waste;

Waste management: temporary storage, transport, and the final destination (reuse, recycling/recovery, landfill and/or incineration).

OPERATION

Emissions

Liquid effluents: characteristics (composition, concentrations, flows/quantities) e.g. WWTP effluent;

Gas emissions: sources, characteristics (estimated composition, pollutants’ concentrations, flows/quantities), e.g.: methane and nitrous oxide emissions generated during the waste water collection and treatment, (depending on transport, treatment, and operating conditions), and during the sludge digestion;

Dust emissions: sources, characteristics (pollutants’ concentrations, flows/quantities);

Noise generation (sources and intensity in decibels) and vibration;

Offensive odours

Waste

Types of waste, sources of waste, e.g.: waste generated by the operation of the WWTP: grit, grease and sludge resulted in different stages of the waste water treatment; waste generated by the operation of the water and waste water network: sludge and sediment collected from the waste water network and other facilities, as part of the cleaning process.

Waste characteristics (estimated composition, humidity, hazardous properties, ELW codes);

Estimated quantities of each type of waste e.g. daily and annually production;

Waste management: temporary storage, transport, and the final destination (reuse, recycling/recovery, landfill and/or incineration.

# An outline of the main alternatives studied by the developer

The development and assessment of alternatives is a requirement under Annex IV(2) of the EIA Directive, which specifies that information provided by the developer according to the Article 5(1) of that Directive (i.e. the EIA Report) should include ‘an outline of the main alternatives studied by the developer and an indication of the main reasons for this choice, taking into account the environmental effects’.

Alternatives are essentially different ways in which the developer can feasibly meet the project’s objectives, for example by choosing an alternative location or adopting a different technology or design for the project. At the more detailed planning level, alternatives merge into mitigating measures where specific changes are made to the project design or to methods of construction or operation to avoid, reduce or remedy environmental effects.

In the case of an WWTP and water and waste water networks projects alternatives would usually be assessed in terms of:

- alternative location;

- alternative design/technologies for the project/main project components.

Pursuant to Article 96(1)(2) of the LEP, the developer is required provide in the EIA report information related to “alternatives of siting (including schemes and bearings of typical points within the established national coordinate system) and/or alternatives to the technologies as studied by the initiator and reasoning of the choice of study made, considering the environmental impact, including a "zero alternative"”. The “zero alternative” is defined in point 26 of the Additional Provisions to the LEP as “the possibility not to implement the activity provided for in the development proposal.”

## Main alternatives studied by developer

Alternative options are usually identified and assessed at the early stages of project development, which clearly represents the most effective strategy for impact avoidance and mitigation.

Key issues for water and waste water infrastructure projects that should be taken into account for the proposed alternatives include but are not limited to:

- the environmental objectives set out in the Strategic Environmental Assessment carried out for regional/urban land use and development plans;

- the requirements set out in land use and development plans, for example, those in relation with the proximity to other existing and future developments, utilities, etc.;

- existence of natural constraints related to topography (e.g. mountains; deep valleys), site hydrogeology and hydrology related aspects;

- constraints induced by protected areas locations, e.g. recommendations of Appropriate Assessment (AA) carried out for a Natura 2000 site;

- existing water and waste water infrastructure in the area and in the region;

- proximity to cities, towns and villages, potentially posing development constraints;

- population density;

- proximity to/interference with transport infrastructure (roads, railways);

- proximity to/interference with important utility lines (e.g. power, gas);

- regulatory requirements regarding drinking water supply, waste water collection and waste water treatment;

- development constraints (e.g. a particular land use; restricted areas);

- contaminated sites;

- land ownership issues;

- interference with scenic routes, or areas of natural beauty.

Where a considered alternative has the potential to affect a protected area included or proposed to be included in the Natura 2000 network, the developer needs to carry out an assessment of the potential impact of the project on Natura 2000 sites, as stipulated in Article 6(3) and (4) of the Habitats Directive at this stage. The results of the AA must be considered during the EIA, and presented in the EIA Report.

The alternatives considered should be relevant and reasonable in terms of the project context. Some examples of alternative locations and design, for the main components of the project are presented in Box 9.

- Alternative locations and design

| Alternative locations |
| --- |
| WWTP | Alternative sites for the location of the WWTP; Use for WWTP location the existing site or other site; |
| Waste water collectors | Alternative routes for waste water collection; Gravity waste water collection versus pressure waste water collection; |
| Water supply network | Different routes for pipelines; Different location for the WPSs or reservoirs (by considering the land use, the elevation of locations, etc.). |
| Maps showing the alternative locations for project components will be annexed |
| Alternative design |
| WWTP | Rehabilitation of an existing WWTP including the sludge treatment facilities (civil structures, equipment) versus construction of a new WWTP; |
|  | A single WWTP for more agglomerations versus WWTPs for each agglomeration; |
|  | Construction of an WWTP versus use of a compact WWTP; |
|  | Alternatives for secondary and tertiary treatment - e.g. activated sludge, fixed film systems (bio-filters, rotating biological contactor, and biological aerated filters used for secondary treatment and nitrification/de-nitrification) and phosphorus chemical removal for tertiary treatment; |
|  | Different disinfection methods - e.g. chlorine, ozone, UV application; |
|  | Sludge treatment: drying, digestion (aerobic or anaerobic), filtering, centrifugation; |
|  | Sludge treatment facilities at WWTP location versus sludge treatment in a single facility, located at another location; |
| Waste water collectors | Rehabilitation of existing pipelines versus new pipelines; |
|  | Combined sewer network versus separated sewer network; for combined waste water network, by location of storm overflow basin, different options depending on technical characteristics; |
|  | Rehabilitation of an existing WWPS (civil structures, equipment) versus construction of a new one; |
|  | Deep sewer trenches and low number of pumping stations versus shallow sewer trenches and more pumping stations; |
|  | Pressure mains collectors versus gravity main collectors; |
| Water supply network | Keeping the existing system configuration versus reconnecting the water distribution system supplied from high level reservoirs and adding extra storage capacity; |
|  | Reservoirs location with a potential for gravity flow into supply versus location that require pumping; |
|  | Construction alternatives, e.g. classical technology – open trenches versus controlled horizontal drilling for pipe laying; |
| Drawings, flow diagrams and/or map illustrating the alternatives will be included. |

As already mentioned above, under Bulgarian national legislation the CA may be integrated into the EIA and within one joint procedure. It can also be carried out as a separate assessment. The CA Ordinance distinguishes in Articles 39 and 40 respectively between the cases when EIA is compulsory under the LEP (Annex I investment proposals) and when it is not mandatory. In any case when it is deemed that EIA would be necessary, the EIA and the CA are carried out together/in parallel. The competent CA authority is obliged to define the scope of the CA report, including as regards the alternatives to be assessed. In that sense the alternatives should be assessed both from the point of view of EIA and specifically as part of the CA, as this is a requirement under the relevant EIA and CA legislation. Of course, Bulgarian national legislation does not limit the assessment of the alternatives only to those identified by the developer. These are also subject to scrutinity during the assessment of the quality of EIA report and the annexed to it CA report. Moreover, as long as Bulgarian law goes beyond the requirement of Article 6(3) and (4) of the Habitats Directive, by making consultations with the competent nature protection authorities and with the public mandatory step of the CA procedure, also provision is made that the alternatives identified at this stage (if such are presented with comments and opinions of the consulted competent authorities and the public) should be assessed.

As already mentioned above, under Bulgarian national legislation the compatibility assessment may be integrated into the EIA and within one joint procedure. It can also be carried out as a separate assessment. The CA Ordinance distinguishes in Articles 39 and 40 respectively between the cases when EIA is compulsory under the LEP (Annex I projects) and when it is not mandatory. In any case when it is deemed that EIA would be necessary the EIA and the CA are carried out together/in parallel. The competent CA authority is obliged to define the scope of the CA report, including as regards the alternatives to be assessed. In that sense the alternatives should be assessed both from the point of view of EIA and specifically as part of the CA, as this is a requirement under the relevant EIA and CA legislation. Of course, Bulgarian national legislation does not limit the assessment of the alternatives only to those identified by the developer. These are also subject to scrutinity during the assessment of the quality of EIA report and the annexed to it CA report. Moreover, as long as Bulgarian law goes beyond the requirement of Article 6(3) and (4) of the Habitats Directive, by making consultations with the competent nature protection authorities and with the public mandatory step of the CA procedure, also provision is made that the alternatives identified at this stage (if such are presented with comments and opinions of the consulted competent authorities and the public) should be assessed.

## Baseline scenario

The existing environmental conditions (including human beings), taking into account the choice of not developing the project, should be described in the Baseline Scenario or the so-called "Zero Intervention Scenario.” Thus, the potential negative effects on the environment should be identified, based on the identification of deficiencies due to the existing situation, e.g.: the needs for repairs of old infrastructure and corresponding costs, failure to comply with applicable regulatory requirements, etc.

## Alternative selection

The information given in this section of the EIA Report will be of such detail as necessary to document the selection process for the preferred alternative in a comprehensible and transparent manner. For this purpose the EIA Report needs to provide reviewers with a summary of the main elements of the analysis that were used to compare the different options / technical alternatives.

The alternative selection is carried out in the early stages of project development with the objective to evaluate and compare feasible development options taking account of several criteria such as technical/engineering, economic, social and environmental. Each criterion is usually expressed by a number of relevant parameters or sub-criteria with their associated indicators. The ultimate comparison and selection of the preferred alternative should be made based on weights that are attributed to each of the key criteria according to their relative importance.

As mentioned in Section 4.1 above, the proposed alternatives can refer to several options that should be compared by quantifying of the significant positive and negative effects, and taking into consideration the “Baseline Scenario”.

The option for an alternative should be justified considering more criteria, such as:

- Environmental criteria: a low adverse environmental impact, considering that the mitigation measures envisaged could be able to reduce the residual impacts to acceptable levels;

- Technical criteria: performance of design, enhanced processes/technologies proposed, etc.;

- Financial and economic criteria: investments cost of the materials and chemicals used, repair and maintenance costs, etc.;

- Social criteria: living conditions in project area, the local economic activity in project area, etc.

# Description of the existing environment (baseline conditions)

The components of the environment that are likely to be affected by a project concerning water and/or waste water infrastructure (during its construction and operation phase), in particular include physical receptors (soil, water, air, climate), biological receptors (flora, fauna), the human environment (human beings, material assets, cultural heritage and landscape) and the inter-relationship of these receptors.

For the EIA Report the description of the existing environmental conditions should provide such information as needed to facilitate the identification and evaluation of the likely significant effects on each receptor. In current practice this description is grouped along the following criteria as explained in more detail below:

- context (project area of influence / study area);

- character (information to be provided for each environmental component);

- the significance and sensitivity of each of the relevant components / receptors; and

- sufficiency of data.

An EIA Report should include a concise description of the existing environmental conditions that are relevant to the project, with references to studies, reports, field surveys, monitoring records, etc., which be added in an appendix of the EIA Report. The description of the baseline information should be focused only on those aspects, which are relevant to the environmental components and could be significantly affected by the project implementation.

The overview of the existing environment should give the information that can be considered as a starting point for a good assessment of the project’s effects, and for the monitoring of project implementation.

## Context

The establishment of appropriate information on the existing environment requires knowledge on the project area of influence or context, i.e. on the spatial extent, timing, frequency and duration of significant impacts that the project is likely to cause. This context needs to be established for all key activities of the project and their associated significant impacts and for each of the affected components of the natural and the built and inhabited environment.

A simple practical approach for establishing this context is to map the various activities / project components and their respective effect areas and boundaries.

The extension of the area of influence may differ from one project phase to the next one. Therefore it is important that the potential areas that may be affected by the proposed project to be identified, and the  baseline conditions description should make reference to them.

## Character

An accurate description of the existing environment (‘baseline’) is necessary to predict the likely significant impacts of the proposed development. The methodology used in undertaking baseline investigations should be well documented to facilitate an understanding of the information and any assumptions made and to ensure that the results of later monitoring can be referenced.

Descriptions should, in the first instance, rely upon published reference to ensure objectivity. Some standard sources of such information are listed in Box 10.

- Standard Sources of Environmental Baseline Information

Topographic maps

Aerial Photographs / Google Earth

Technical information from local, regional and national Government (reports, monitoring data and thematic maps, e.g. on soils, geology, climate; hydrology, water quality, importance protected areas, zoning plans, inventories of protected features of cultural or historic importance, etc.)

Scientific and technical reports / publications

Other approved SEA reports and EIA Report prepared for projects in the same region / area

Publications from professional, research and NGO organizations

All sources of information (maps, illustrations, statistical and technical data, monitoring data, specialist statements etc.) must be up to date and adequately referenced. As a rule, maps and figures should be of good quality and easy to read.

The information provided in this section of an EIA Report should be possibly concise rather than reflecting the amount of environmental data that may be available on a specific issue or for a given area. The guiding principle is to provide such baseline as required to assess the sensitivity of a specific environmental component or function with respect to the subsequent impact assessment and decision making. Only where specifically critical issues have been identified at the scoping stage additional detailed information may need to be presented.

The below list includes several issues with regard to the environmental baseline conditions, but in the EIA Report should be presented only those that are relevant for the environmental impact assessment of the proposed project, and for the necessary corresponding mitigation measures.

### Surface Water and Groundwater

- Relevant information from strategies/plans on national or regional level (River Basin Flood Strategy, River Basin Development Plan, River Basin Management Plan):

- quality targets for groundwater and surface water bodies, set for the project area through River Basin Management Plans;

- predictions of overflow/flooding events (frequency and volume); current overflow/flooding events (frequency and volume).

- Surface water bodies in the project area and in its vicinity:

- tributaries and confluents of the receiving water body of the WWTP effluent  with other surface water bodies;

- rivers, streams etc. crossed by waste water or water supply pipelines (according to projects characteristics) e.g. sewage collectors or sewage pipes (existing or proposed within the project), water main transmission, distribution networks (existing or proposed within the project, etc.); brief description of the location of the crossings, distances to project location/s;

- present and potential water use of water bodies (in project area): e.g. source of drinking water, source of industrial water supply, irrigation, fishing, recreation, etc.;

- discharge points of water polluters or potential polluters in the water bodies located upstream or in the project area, e.g. industrial, non-treated water, farming, etc.;

- Data on the water body receiving the WWTP effluent:

- physical and chemical parameters, nutrients, pH, etc.;

- flows, volumes; seasonal variations of surface water bodies with regard to the quality parameters, and flows;

- river bank stability for the concerned surface water bodies (e.g. pipe crossings, the WWTP outlet pipe, etc.);

- extent and maximum levels of any recorded flooding.

In the case of an existing WWTP rehabilitation: current waste water discharged flows, and key parameters of the waste water, e.g.: TSS, BOD, COD, N, P, TDS, etc.

  - Groundwater:

      - nature and location of the aquifers in the project area;

      - groundwater flow directions;

      - groundwater interaction with surface water; interaction with sea/salt water; vulnerability to pollution;

      - groundwater quality in project area; if existing pollution or contamination hazards have been identified in the groundwater in the project area, additional data will be included;

      - depth to water table, mainly in the proposed work locations and on pipelines routes.

  - Sanitary restricted area in the vicinity of the proposed routes of water and waste water network, and afferent civil structures and installations (WWTP, WWPS, overflow basins locations water main transmission, drinking water network,  DWTP, WPS, reservoirs);

  - Current water consumption (l/day/cap) in the project area;

  - Drainage in the project area; the location and specification of canals, drains and rivers; identification of areas prone to flash floods;

  - Map: river basin catchments map and indication on the map of the main project works locations, water users.

### Soil and Geology

    - Project area topography (maximum and minimum elevation, and maximum and minimum gradients);

    - Pedological features of the project area;

    - Geotechnical features of the project area, usually provided by a hydrogeological study;

    - Exploration for natural resources in project area and in the region (minerals, oil, water supply, etc.);

    - Soil contamination in the project area; any previous or recent investigations, and the comparison of investigations conclusions with the  land use requirements;

    - Soil degradation in the project area: surface erosion, depth erosion, landslides, soil settlement – compacting;

    - Maps showing the topography of the area as well as pedological and geological features of the region are useful for a better understanding of soil and geology aspects.

### Air and climate

    - Climate and atmospheric conditions: precipitation, evaporation, wind directions and frequency of occurrence, temperature, seasonal variability;

    - Projected increase in extreme weather conditions, such as prolonged dry periods, rainstorms, heavy snowfall, etc.;

    - Data on existing air quality in the project area;

    - Sensitive locations to air quality in the project area and neighbourhoods;

    - Data related to nuisance caused by odours and recorded complaints from the public regarding offensive odours;

    - Records of exceeded concentrations of hydrogen sulphide and/or ammonia (diffuse emissions sources).

### Human beings

    - Administrative locations of the project area;

    - Geographical description of the project area;

    - Current and future residential areas (as stated in the plans of land use and urban/rural development);

    - Distances from main proposed works to residential, commercial and recreational areas, institutions and other sensitive receptors;

    - Occupation, activities related to the inhabitants in the project area; where relevant, indication of the time, duration or seasonality of any of those activities;

    - Disease rates related to water use in project area, risks on human health;

    - Noise-sensitive locations of the project area and the vicinity of the main proposed works;

    - Noise levels in works locations;

    - Maps: geographical map/administrative map - indicating the locations of sensitive receptors.

### Fauna and flora

    - Description of the vegetation of the project area and its vicinity:

  - habitats or plant communities, locations of sensitive or rare species;

  - dominant species, species’ diversity, dependence on particular environmental factors, existing management;

  - principal habitats, significant locations for breeding, sites for survey/trapping;

- Description of the fauna of the project area and its vicinity:

  - diversity, population size or density of fauna, existing management;

  - special requirements: territory size, habitat quality, current management, lack of disturbance;

  - presence of any habitat, plant or fauna species that is internationally, nationally, regionally or locally rare, especially protected species;

  - the importance of water as a habitat, in the region - very important especially for the areas located downstream to the outlet discharging the effluent of WWTP.

- Natura 2000 sites in the project area and its vicinity:

  - Natura 2000 sites identified (name and code of Natura 2000 site), locations, distances from the site to project location, species and habitats of Community interest in the site, site management;

  - description of the AA procedural stages carried out under Article 6 of the Habitats Directive (if applicable);

- Natural protected areas other than Natura 2000 sites identified in the project area and its vicinity;

- Maps showing the main characteristics of project area for the above-mentioned aspects.

### Landscape

- Characteristics and geomorphology of the relief in works locations;

- The landscape on project works locations and in the surrounding area;

- View of the works locations from adjacent properties and public, areas particularly where these are sensitive, e.g. residential, recreational or turistic areas;

- Land Development and Use Plan requirements and regulations for project area in relation with landscape;

- Maps showing the main characteristics of project area for the above-mentioned aspects.

### Material assets

- Cities, towns, villages and settlements in the project area;

- Utilities in the project area (water supplies, waste water collecting system, power systems, canals etc.);

- Industry, economic objectives in the project area;

- Residential, tourist and recreational areas in project area and in the vicinity;

- Isolated public & private objectives for residential, commercial, industrial, recreational or social purposes (individual properties for housing, schools, camping and other recreational plots including hospitals, zoo parks, facilities for old people);

- Land development planning requirements and regulations for the project area;

- Maps showing the main characteristics of project area for the above-mentioned aspects.

### Cultural heritage

- Architectural, archaeological heritage in project area or in the vicinity;

- Important architectonical or archaeological objectives located the vicinity of works proposed by project; distances to these objectives will be specified (a map showing the objectives locations will be provided);

- Restrictions, special conditions imposed by national and local authorities;

A list of all information sources should also be provided.

## Significance

The significance of areas or sites is determined by the designation, quality or value that is assigned to this aspect of the existing environment. Questions to be addressed here are:

- Is the site or area protected/planned to be protected by legislation (international, national, and local) or by designation for its ecological, landscape, cultural or other value?

- Are there important water uses of receiving water body (e.g. raw water abstraction for drinking water production, irrigation, fisheries, recreation etc.), in the project area and downstream?

- Is the site or area renewable, unique, or replaceable?

- Is the site or area scenic, ordinary or derelict?

## Sensitivity

The sensitivity of an area, site, or function relates to the question whether the permanent, temporary or accidental effects caused by the project would significantly alter the character of a relevant environmental factor, for example:

- Would any increase in nutrients cause eutrophication of a specific habitat?

- Would downstream water users be affected by treated waste water discharged into receiving river?

- Would the soil degradation be accentuated (e.g. by erosion) by performing the construction activities?

- Would the soil degradation be accentuated (e.g. by erosion) in certain areas by performing the construction activities?

## Sufficiency of data

Data and information provided in the EIA Report must be of such quality and completeness as to allow the competent authority to make a sound and informed decision on whether to grant or withhold consent to develop the project. Criteria that may guide the assessment of sufficiency of data contained in an EIA Report are:

- Is the information that is necessary for identification of the main effects available?

- Is the information that is required for the assessment of the main effects available?

- Is the information focused on the effects, which are likely and significant?

The certainty or confidence which the information provides is a good basis for evaluating the quality of data. Where information provided in an EIA Report is incomplete, it must be clearly indicated that the missing information was not withheld intentionally. This approach will ensure that all parties are aware of the incompleteness and of the fact that the decision will be qualified or conditioned on the information being provided at a later stage.

# Description of the likely significant environmental impacts and mitigation measures

The projects concerning the development of water supply infrastructure, waste water collection systems and urban waste water treatment have significant positive effects, such as:

- positive effects on the quality of the groundwater and surface water by reducing the number and frequency of sewage overflows;

- positive effects on the quality of the groundwater by minimization of leakages of the existing collectors of waste water;

- proper water supply and waste water collection services, with benefits to those living and working in the project area or neighbourhood(s).

Despite of their positive effects, the implementation of the projects could require consideration of possible negative implications.

## Prediction of the likely significant impacts

The prediction of the likely significant effects should be done by considering the environmental baseline conditions and, their description should cover “the direct effects and any indirect, secondary, cumulative, short-, medium and long-term, permanent and temporary, positive and negative effects of the project”.

The parameters taken into consideration in impact prediction and decision-making have to include the following characteristics of the environmental impacts:

- nature (positive, negative, direct, indirect, cumulative);

- magnitude (severe, moderate, low);

- complexity;

- extent/location (area/volume covered, distribution), local, regional, global, transboundary nature of the impact;

- stage (during construction, operation, decommissioning, immediate, delayed, rate of change);

- duration (short-, long-term);

- frequency (intermittent, continuous, periodic);

- reversibility/irreversibility;

- likelihood (probability, uncertainty or confidence in the prediction); and

- significance.

The likely significant effects of the different project activities during construction, operation, and decommissioning phases should be identified in this section of the EIA Report. Various methodologies could be applied for assessing environmental impacts having the following steps:

- Impact definition - identify impacts in the context of the baseline conditions and create a preliminary matrix of potential environmental impacts (adapted for specific types of projects) positive and adverse, of different project stages on environmental parameters;

- Assessment of significance of identified impacts -  interpret impact significance based on a ranking method (for example based on spatial, temporal and intensity parameters) for the adverse impacts from the preliminary matrix;

- Assessment of cumulative impacts;

- Assessment of transboundary impacts;

- Selection of mitigation measures - select the moderate and major impacts as likely significant impacts and proposed mitigations measures; present them in a table for every environmental component and project phase;

- Assessment of residual impacts.

Some examples, related to frequent adverse (negative) effects and measures for their mitigation are presented in the following subsections.

## Description of the likely significant environmental effects and their mitigation

The next subsections present a selection of likely significant environmental impacts and related mitigation measures for waste water collection systems and waste water treatment projects. The following tables may thus be used as a kind of checklist for likely significant effects of the project.

The selection of the mitigation measures has to be based on the mitigation measures hierarchy considering the following options, as several EU directives refer (i.e. the Habitats Directive):

- avoid and/or reduce at source – the cause of impact is redesigned or altered;

- mitigation at source (in-situ) – “end-of-pipe” measures (on-site measures);

- mitigation at receptor – implemented when impact cannot be avoided on-site and off-site measures have to be implemented;

- compensation - compensation for the loss, damage and the general intrusion when other mitigation measures are not possible or fully effective.

The higher-level measures are usually cheaper, more politically acceptable, preventive/precautionary, and with fewer social/equity implications than the lower level ones.

Some mitigation measures are adopted in the early stage, of designing by choosing of less pollutant technologies, and others are expected as part of good international practice.

Pursuant to Article 96(1)(4) and (6) of the LEP, the EIA report should provide:

- a description, analysis and assessment of the potential significant effects on the population and the environment resulting from implementation of the development proposal and information on the use of natural resources and emissions of harmful substances in normal circumstances and in an emergency, generation of waste and creation of nuisances

- a description of the measures envisaged to avoid, reduce and, if possible, remedy significant adverse effects on the environment, as well as a plan for implementation of the said measures.

### Surface water and groundwater

The implementation of a project concerning waste water infrastructure can result in changes of the receiving water body characteristics due to the discharging of WWTP effluent, and due to its pollutant concentrations and load.

In this context, for the identification of the effects on receiving water bodies, the issues that must be taken into account are usually related to:

- polluting load of WWTP effluent;

- average and dry weather flow of receiving water body;

- average and dry weather flow of WWTP influent;

- pollutants concentrations of WWTP effluent;

- pollutants levels (concentrations and loads) on receiving water body and

- the targeted reduction of polluting loads (kg/day, t/year) and concentrations (mg/l) of water quality parameters (in connection with waste water treatment requirements), as stated in the RBMP.

Therefore, a comparison will be made of the WWTP effluent concentrations and those of the receiving water body, under existing and future conditions. Such a comparison will take into account the limit values, which are set up in the relevant RBMP.

- Likely significant effects on water and groundwater, and their mitigation

| Likely significant effects | Mitigation measures |
| --- | --- |
| CONSTRUCTION |
| Disturbance of groundwater level as a result of excavation works | Safe drainage and evacuation of the pumped groundwater, in order to avoid possible suffusion phenomena |
| Temporary changes of hydraulic characteristic of the surface water bodies - level, velocity, flow - caused by construction works on river bed or on river banks (e.g. WWTP outlet pipe, pipelines crossing a river or a stream) | Use of adequate construction techniques to eliminate consistent modifications of the surface water body morphology |
| Modifications of surface water flow sections through: soil wash and rocks displacing into the surface water body stability degradation of surface water body banks because of placement or operation of construction equipment in the area | Timing of construction activities and avoidance of the execution works under aggressive weather conditions (rains, strong winds); Construction works for stream and river crossings during low-flow periods; Use special construction techniques in areas of steep slopes, exposed to erosion phenomena; also, in the areas of stream crossings; Avoidance of performing the construction works simultaneously on both river banks; Avoidance of creating excessive slopes in the vicinity of river banks; Measures for protection against erosion, corresponding to the characteristics of the working area; Limitation of the excavations size within the 100-year floodway of the surface water bodies. |
| Surface water body pollution through the runoff of sediment as a result of erosion or of landslides |  |
| Pollution of surface water bodies through rain water runoff from construction yard and/or working site, in case of inappropriate facilities for storage of construction materials, hazardous substances, fuel, lubricants and waste | Procedures for the storage and handling construction materials, hazardous substances, fuel, lubricants and waste; Storage fuels, lubricants and chemicals in proper storage facilities (restricted access, sealed packages); Tanks for fuel storages leak-proofed and installed on impermeable surface; in the case of incidental spills collecting recipients, absorbent material and fire fighting equipment shall be provided; Covering construction material stockpiles (with tarpaulin or similar). |
| Pollution of the surface water body because of domestic or industrial waste water discharges from construction yard or from working sites | Waste water treatment corresponding to the waste water receiver quality category (temporary sanitary facilities - portable chemical toilet, oil separator or grease trap); Periodical control and proper maintenance of waste water treatment units. |
| In the case of rehabilitation/extension of WWTP or in the case of a new WWTP construction at the same location with existing WWTP: pollution of receiving surface water body through the discharge of untreated waste water or partially treated waste water. | Maintaining at least partial operation of the existing WWTP, during execution of construction works |
| Groundwater pollution through the infiltration of accidental spills (e.g. fuel and lubricants, hazardous substances) because of improper storage facilities, refuelling operations or handling operations | Storage of fuels, lubricants and chemicals in proper storage facilities (restricted access, sealed packages); Procedures for storage and handling of the construction materials, hazardous substances, fuels; Fuelling of the vehicles and equipment at workshops/sites with adequate leakage prevention (e.g. impermeable surface, settlers and oil separator); Emergency procedures and contingency plans for accidents, breakdowns, spills, etc. |
| Wastage of drinking water resources | Use of low quality water for sprinkling for dust prevention at the construction yard and work sites; |
| OPERATION |
| In the case of new WWTP - WWTP effluent discharge consist a source of pollutants for the receiving water body | Appropriate treatment of waste water, to ensure natural regeneration capacity of surface waters. |
| Pollution of receiving water body because of waste water treatment failure, which can be caused by: increased loads of pollutants in WWTP influent through exceeded polluted waste water discharged into WWCS (from industrial users, commercial users and other non-domestic waste water); malfunctioning of WWTP because of failure of electric supply, failure of electrical and mechanical equipment, improper operation of WWTP equipment. | Control and reducing measures, for discharges from industry, commercial users, etc. into waste water collecting system, implemented by WWTP and collecting system operator; the framework of these activities should be included in an action plan that will establish the measures for limiting the potential impact on the WWTP treatment process. The main measures recommended to be included in the action plan will refer to: full inventory (quantitative and qualitative) of industrial effluents as well as drainage systems; the inventory should be accompanied, where suspiciousness of potential pollution is identified, as well as where polluting episodes were recorded, by a sampling and analysis campaign; where the above mentioned effluent inventory indicates a risk that the limit values of waste water parameters could not be met (or could not be met at all times), special conditions have to be applied by the WWTP operator to the industrial companies; Inspection and control programme implementation by the WWTP operator to industrial companies (e.g. pre-treatment facilities, the need of upgrading pre-treatment facilities, waste water flows metering, self-monitoring); Emergency plan for accidental pollution events on industrial companies’ locations. Developing and implementing of Emergency response programme for the WWTP operation, which will address issues such as: emergency backup power; operational monitoring programme for WWTP and procedures for WWTP operation; inspection procedures to determine the current conditions; preventive maintenance programme; alarm systems at key points in the treatment process; emergency operational plan; back‐up equipment. |
| Water wastage due to degradation of the water supply pipes | Regular inspections in order to timely detect any failures, and take appropriate remedial action; Emergency plan for accidental events and damages at WSS (e.g. rerouting and a temporary shutdown). |
| Groundwater pollution through infiltration of leakages as a result of damage occurrence of civil structures, platforms, pipes etc., which are located at the site of the WWTP | Regular inspections in order to timely detect any failures, and take appropriate remedial action; An emergency plan for accidental pollution events and damages on civil structures, platforms, pipes; Compliance with construction requirements for sludge storage location, and those related to water impermeable basis; A monitoring programme for groundwater (water table) in the WWTP area; generally it is recommended to have at least two monitoring wells, placed up and downstream the WWTP location, considering water movement direction of groundwater. |
| Groundwater pollution (at WWTP location) through infiltration of leaks into the soil, during certain activities (e.g. vehicles refuelling and/or washing) | Restriction of such activities in the absence of appropriate facilities; for emergency situations, strict control and prevention measures should be applied |
| Receiving water body and/or groundwater pollution - in the case of physical damage occurrence on WWCS. Particular case – pipeline damage on the surface water body crossing or along marine shorelines. | Regular inspections of the WWCS in order to timely detect any failures, and take appropriate remedial action; Emergency plan for accidental pollution events and damages on WWCS; Placing the main pipeline inside a protective pipeline. |

### Soil and geology

- Likely significant effects on soil and geology, and their mitigation

| Likely significant effects | Mitigation measures |
| --- | --- |
| CONSTRUCTION |
| Soil degradation as a result of humus layer removal | Topsoil removal and storage in separate piles and reinstallation after refilling of the trenches, to enable natural revegetation; Soil stripping and clearance of vegetation to be done parallel to contour lines, starting from high to low ground; Utilisation of appropriate machinery for land clearing to minimize disturbance to the soil. |
| Soil compaction on working site, and consequently, reduced capacity for infiltration of the precipitation | During the construction period: perform the construction works for stream and river crossings, during low-flow periods; provision of the perimeter drains to intercept storm-runoff from outside the working site; in severe situations: sand/silt traps and sediment basins; At the completion of the works: ripping of the soil, re-application of the top soil and establishment of vegetation cover. |
| Temporary land use change | Restoring the site upon the completion of work |
| Soil erosion (especially the areas situated in sloping areas) through: excavation works (at working area along pipelines routes or at the locations of civil structures), leading to soil instability and landslides; removal of vegetation, earthworks and the use of heavy machinery during construction activities. | Restriction as far as possible the execution of major earthworks to the dry season; Drainage of work sites to facilitate run-off discharge, and if possible, treatment for reducing silt loading (sedimentation); Application of appropriate erosion-protection measures: sequence of works to avoid areas subject to erosion during severe storm events, execution of silt screens, in particular where it concerns works situated in sloping areas and in riverbanks; Implementation of active revegetation programme at work sites, including in particular erosion-prone areas (e.g. hill sides and riverbanks); |
| Soil pollution at the location of the construction yard and work sites because of the accidental spillage of fuels and lubricants at parking areas, fuelling and cleaning of vehicles and equipment used for construction activities | Parking area arrangements for equipment and vehicles involved in construction activities (e.g. impermeable surface); Maintenance, fuelling and cleaning of vehicles and equipment done at workshops/sites with adequate leakage prevention (e.g. impermeable surface, settlers and oil separator); Storage of the fuels, lubricants and chemicals in appropriate storage facilities (restricted access, sealed packages); Tanks for the fuel storages leak-proofed, and installed on impermeable surface; in the case of incidental spills collecting recipients, absorbent material and fire fighting equipment shall be provided; Proper maintenance of the transport and construction equipment; Clean up procedures for the construction equipment. |
| Soil pollution at the construction yard and working sites by accidental spillage of chemicals, and by infiltration of leachate from uncontrolled deposits of waste | See mitigation measures for groundwater pollution through infiltration of accidental spills |
| Failure of infrastructure such as steel piping or concrete foundations because of the corrosive nature of the soils | Appropriate construction procedures and construction materials use to manage the potentially dispersive and corrosive nature of the soils on site |
| OPERATION |
| Soil erosion and landslides in sloping areas, caused by run-off to surface waters and/or by removal of vegetation | Implementation of active revegetation programme on works sites, including in particular erosion-prone areas; Application of appropriate erosion-protection measures, according to the characteristics of affected area. |
| Soil pollution at the WWTP location, through leakages because of damage to pipes, basins, structures | See mitigation measures recommended for groundwater pollution due to infiltration of leakages because of the damage occurrence to civil structures, platforms, pipes etc. on the WWTP site |

### Air and climate

- Likely significant effects on air and climate, and their mitigation

| Likely significant effects | Mitigation measures |
| --- | --- |
| CONSTRUCTION |
| Air pollution - fugitive dust emissions during construction activities through entraining dust from the working site by vehicles, earthworks, and due to the wind erosion from open areas and stockpiles | Prevention of the dust through sprinkling, during periods of dry weather; the water should not be applied in excess, otherwise runoff and mud resulted from the site could be transferred onto public roads by vehicles; Daily cleaning of the access ways - in the neighbourhood of the construction yard and working sites (removal of the earth and sand to prevent dust). |
| Air pollution through fugitive dust emissions generated by construction materials handling operations | Procedures for handling operations of construction materials; Control and clearing of loose materials. |
| Air pollution through emissions from motor vehicles, transport and construction motor equipment | Regular inspections of the vehicles and equipment; Limitation of working hours for the works located in sensitive locations. |
| OPERATION |
| Offensive odour due to inappropriate maintenance operations, or dysfunctions of the WWCS | Regular inspections and de-clogging operations of the WWCS, especially of gravity sewers to prevent hydrogen sulphide emissions; WWPS - prevent sludge accumulations (e.g. backup equipment); Pipelines prevent sludge accumulations, for example by flushing with fresh water. |
| Odour generated by WWTP and WWPS activities | WWTP and WWPS placements at a certain distance from human settlements; moreover, the location of these works should take into account the prevailing wind direction (to blow on the contrary direction from residential areas); Monitoring the operation of the WWTP in order to optimize the treatment process and avoid expel of odours; Odour abatement measures: minimisation of the time for sludge retention in primary settlement stage of the waste water treatment; applying extended aeration to avoid primary settlement stage of the waste water treatment; appropriate handling and removal of grit/grease and other waste resulted from maintenance activities; control sludge treatment process; monitoring of the parameters for sludge treatment process ; control of the waste water flow, and the aeration in waste water treatment process; covering WWTP works (inlet works channels, screens and pump stations basins, etc.) and applying of odour abatement techniques: biological abatement techniques (e.g. bio-filters, bio-scrubbers) and non-biological abatement techniques (e.g. wet chemical scrubbing, dry chemical scrubbing/adsorption); extracting odours to an odour control treatment system such as biotrickling filtration and carbon filtration; covered skips for screenings and grit; minimisation of screenings and grit storage on the site; Control and minimisation of odours from other residual materials and waste, e.g. imported sludge, septic tank waste, etc.; Planting of vegetation (trees and plants of varying heights forming a windbreaker) at the borders of the WWTP site. |
| Offensive odour on transport routes of sludge and other waste resulted from waste water system operation | Avoidance the crossing of the urban area, especially crossing the sensitive locations – alternative routes for sludge transport (final destination) |
| Greenhouse gas emissions (methane, nitrous oxide and carbon dioxide): emissions generated during waste water transport; emissions generated during the waste water treatment (especially the secondary waste water treatment), and the anaerobic digestion of waste water sludge; | Control of the waste water quality discharged into the WWCS; Perform periodically de-clogging and maintenance operations of the WWCS components taken into consideration that methane generation typically occurs in areas of high chemical oxygen demand and low oxygen concentration; Aerobic treatment of the waste water; Aerobic stabilisation of the sludge resulted from waste water treatment; Use of efficient aeration systems and keeping them cleaned and well maintained; Covered structures for the waste water treatment units; gas capture and combustion systems to flare the methane and use it for onsite generation of electricity or other thermal uses. |

### Human beings

- Likely significant effects on human beings and their mitigation

| Likely significant effects | Mitigation measures |
| --- | --- |
| CONSTRUCTION |
| Traffic disruptions, resulting in nuisance and interruption of commercial and social activities (especially during pipelines construction or rehabilitation) | Preparation of a traffic management plan which will address aspects related to following issues: phasing of construction activities, rerouting of the traffic; scheduled construction activities for minimisation disruption of existing traffic patterns to residential and businesses areas; establishment of temporary access ways (with collaboration and with assistance of local traffic police authorities) Parking restriction of construction vehicles in front of access points and/or business parking areas; Informing the local communities of the construction programme, for example, through local newspapers; Temporary covering of open trench segments to allow residents and service vehicles to access driveways Limitation of any temporary interference with private property (e.g. pipeline crossings over private lands); Limitation of the length of trenches at one time as much as possible - period estimation of construction works will be done; Restriction of materials delivery or removal during peak traffic hours along major road arteries. |
| Safety problems caused to the general public by excavations | Protection (fencing) and signalling of work sites (especially excavation works), in particular during the night, with clear marking of the safety border of the works perimeter (main locations will be specified on a map); Restricting access to working sites for other persons than authorised workers (places occupied by operation mechanical and electric equipment, open trenches). |
| Disturbances and nuisances to the public, through air emissions (dust produced at work sites, as well as resulted from the transport of raw and waste materials) and odour from waste stored at work sites | See mitigation measures recommended in subsection 6.2.3, for similar causes of air pollution and odour |
| Discomfort for the inhabitants due to the noise generated by construction activities | Interdiction of construction activities at night and restrictions on limits on hours of rest in sensitive neighbourhoods (e.g. hospitals); Noise mitigation measures e.g. noise barriers, use of electrical equipment/ installation rather gasoline/diesel-powered; Restrictions of speed limit and of tonnage for heavy vehicles passing through residential areas; Proper maintenance of equipment for quiet operation. |
| OPERATION |
| Changes in the quality of water supplied because of disruptions, malfunctions, etc. of the water supply infrastructure | Monitoring of water quality in different points of water distribution network and take appropriate remedial action; Regular inspections of the water supply system in order to timely detect any failures of the system, and take appropriate remedial action; Public notification of population and information in case the water quality is affected and improper for consumption. |
| Drinking water contamination due to development of potential pollution activities in the vicinity of water supply network and afferent installations | Delimitation of the restricted areas in the proximity of WPS(s) and reservoirs location and along the main water transmission; Periodically inspections for checking the compliance with water management regulations related the prevention of water resources pollution. |
| Disturbances and nuisances to the public, through the offensive odour generated by the operation of the WWTP, WWPS or waste water network | See the recommendations in subsection 6.2.3, for mitigating the generation of offensive odours |
| Disturbance to neighbourhoods, as residential, schools, hospitals, recreational areas, etc. through noise and vibration produced by installations and equipment in operation | Insulating the pump houses; Use of low noise and vibration installations and equipment. |
| Maintenance activities of the water supply and WWCS will have similar effects on human settlement and objects of interest as those described for the construction phase, but at a much smaller scale | Regular inspections of the waste water system will be undertaken in order to timely detect and failures of the system, and take appropriate remedial action; For interventions for implementation of repair and maintenance activities the same mitigation strategies and measures should nbe applied as those for the construction phase. |
| Fly and mosquito breeding and disease transmission | Implementation of measures to prevent and control biting insect populations, e.g.: improved drainage of wet areas; regular treatment of affected areas with chemical insecticide (used but only after careful evaluation of any adverse health or environmental effects and with the necessary consents); in the case of sludge drying lagoon: chemical additions. |

### Fauna and flora

- Likely significant effects on flora and fauna, and their mitigation

| Likely significant effects | Mitigation measures |
| --- | --- |
| CONSTRUCTION |
| Affecting fauna species that have a seasonally variable vulnerability due to, for example, breeding, critical feeding times or seasonal migrations | Manual execution of works through elimination of using any equipment and vehicles in protected sites or sensitive areas; Restriction of construction works during the breeding seasons. |
| Change of the covert and food places for fauna species, with habitat in the works area, because of disturbance produced by construction activities | Limiting the speed of the heavy vehicles in sensitive areas; Workers’ training regarding the provisions of the biodiversity protection legislation, and the appropriate mitigation measures. |
| Disturbance of a habitat of fauna species used as ecological corridor to other isolated habitats of ecological importance | Provide bio-corridors/unhindered passages for fauna species; Workers training regarding the provisions of the biodiversity protection legislation, and the appropriate mitigation measures. |
| Total or partial destruction of the vegetation in works areas (soil stripping, vegetation cuttings and clearness); Low ability to recover of the fauna species (either naturally or with assistance) from the habitat disturbance. | Conservation of trees and other vegetation as much as possible; Conservation of trees and other vegetation as much as possible to the largest possible extent; Removal of trees and replanting, avoiding from cutting them down; clearing and cutting of trees shall only occur with the appropriate authority’s consent; An inventory of trees to be cut down shall be made and a plan for replanting will be developed and implemented; After any intervention that may disturb natural sites: ecological restoration through environmental engineering (restorations, rehabilitation) shall be undertaken, including restoration of top soils and (re-) introduction of genetic species to re-establish the natural local ecology; Restriction/control of any fertilizers used during vegetation restoration on affected areas. |
| Aquatic environment alteration due to the changes of water characteristics (physical, chemica, and biological), caused by water body pollution (the causes for pollution described above see subsection 6.2.1 and 6.2.2) | See recommended mitigation measures in subsection 6.2.1 and 6.2.2 – for construction phase |
| OPERATION |
| Alteration of habitats or the species, modification or destruction of migration routes for terrestrial and aquatic fauna because of the land use change | Compensatory planting or restocking of indigenous species; Carry out the efficient elimination of any eventual spreading of the dangerous invasive species ; Creating opportunities for fauna migration or provision of new habitat; Monitoring the affected protected area for a certain period (e.g. 2-3 years), recommended at the beginning and at the end of vegetation period; if any restoration of the flora elements failed, certain corrections and additional planting plan should be started. |
| Aquatic environment alteration caused by changes on water characteristics (physical, chemical, and biological) - caused by water body pollution (the causes for pollution described above see subsection 6.2.1 and 6.2.2) | See recommended mitigation measures for the operation phase in subsection 6.2.1 and 6.2.2 |

In addition, in the case of protected sites located on project area or its vicinity: if an AA was carried out, the EIA Report should include its findings - the significant effects predicted, mitigation and/or compensation measures recommended.

### Landscape

- Likely significant effects on landscape and their mitigation

| Likely significant effects | Mitigation measures |
| --- | --- |
| CONSTRUCTION |
| Visual disturbance from construction yard location and through the traffic associated with the construction activities | Restriction of the size of construction sites; Conservation of vegetation around the construction yard (if present) as much as possible in order to serve as visual shields; Adequate organization and maintenance of the construction sites through good housekeeping; Restoration of construction sites directly upon completion of works (deadline is recommended to be provided). |
| OPERATION |
| Impacts on the area, in particular visibility from the viewpoint of recreation area, tourist area, residential area, etc. | Adequate screening and design of civil structures (WWTP, WPS, WWPS) to ensure that it blends into the surrounding environment; Tree screens at the location of WPS, WWPS and WWTP. |

### Material assets

- Likely significant effects on material assets and their mitigation

| Likely significant effects | Mitigation measures |
| --- | --- |
| CONSTRUCTION |
| Damage to other infrastructure (roads, water supply pipelines, drains, buildings, utility lines, etc.), and therewith lead to a (temporary) disruption of certain public services; Temporary interruption of industrial, commercial and social activities caused by limitation of drinking water supply during construction activities. | Avoid interference with other infrastructure; Coordination of works with other utilities owners, regarding crossings locations (water supply, waste water, telecommunication lines, gas, electricity, etc.); In case of any damage, the execution of repair works as soon as possible (time limits referred in the emergency plan for accidental pollution events, damages to drinking water distribution network, etc.); If any restriction or limitations are required by other utility network owners, these should be precisely scheduled. |
| Temporary interference with private property (e.g. pipeline crossings over private lands) | Where private land or other property is affected, or where there is loss of income as a result of the project activities, it should be agreed on mitigation or compensation measures with the affected population prior to the start of construction |
| Temporary disturbance to residential and other sensitive receptors (hospitals, schools etc.) through generation of noise; Traffic disruption because of construction/ rehabilitation activities (mainly those related to the water distribution network). | See mitigation measures recommended in subsection 6.2.4 Human Beings |
| Damages to civil works (because of vibration) | Identification of vulnerable civil works placed in the immediate proximity of construction sites and use of safety methods and equipment; Elimination the use of equipment that may generate dangerous vibrations; If significant damage can occur, it is recommended to change the location of works. |
| OPERATION |
| Restriction of water quantities supplied (to people, industry, other consumers) in the case of damage on water supply network | Informing the local communities about the duration of repair works; Distribution within the affected area of alternate supplies: water tanks, bottled water; Promotion of reduction of water use and wastage. |

### Cultural heritage

- Likely significant effects on cultural heritage and their mitigation

| Likely significant effects | Mitigation measures |
| --- | --- |
| CONSTRUCTION |
| Damaging of uncovered objects of cultural and archaeological significance not known before | Carry out detailed archaeological survey of site as well as comprehensive desk study to determine level or potential level of cultural or architectural significance of the area; In the case of identifying of any potential archaeological objects, the activities should stop; archaeological authority must be consulted to determine appropriate mitigation measures. |
| Damage to the constructed environment, including architectural and archaeological monuments, through vibrations produced by the construction equipment and construction activities | Use of safety methods and equipment; if the case, termination of the use of equipment that may generate dangerous vibrations; If significant damage can occur, change location of the works is recommended – e.g. alternative location for WPS, WWPS, pipeline route. |
| OPERATION |
| Damage on constructed environment including architectural and archaeological monuments, through vibrations produced by operating the equipment and installations, which serve water supply or waste water infrastructure | Same mitigation measures as recommended for construction phase; Performing of "in situ" protection works in the case of significant threat occurrence to a cultural heritage structure. |

## Residual impact assessment

Residual impact is defined as the consequences of the impact after implementing the mitigation measures. It has to be considered in relation with the baseline conditions, since different baseline conditions can cause different impact significance for the same type of project.

The scale of the residual impact must be assessed using models, e.g. to determine the concentration of key pollutants linked to the associated activities at the receptor location, and following an adequate methodology.

## Cumulative impact assessment

According to the provisions of Annex IV(4) of the EIA Directive, as implemented in Bulgarian national legislation by Article 81(5) and Article 96(1)(4) of the LEP and Article 12 and Article 14(1)(4) of the EIA Ordinance, an EIA also needs to consider the potential indirect and cumulative impacts of his project as well as impact interactions.

Several effects of certain projects can act in different ways on the environment (population, fauna, flora, soil, water, air, climatic factors and material assets, including the architectural and archaeological heritage, landscape). The actions depend on the project location, the characteristics of baseline environmental conditions, for example, sensitive receptors in the project area or in the vicinity but also depending on certain effects of other projects (current and future) and activities, which overlap with the proposed project area.

In this respect, other current and future projects that can be considered are the on-going projects and projects identified in a development plan for the region (approved or in process of approval).

Examples of projects categories that should be addressed, at construction phase or operation phase, in proposed project area or near it:

- urban development projects as extension or rehabilitation of water and waste water networks (in the case of a project concerning a WWTP), development of residential or recreational areas;

- roads projects;

- hydro-technical works such as dams, networks for flow deviation, flood protection/prevention works;

- industry.

Examples of the possible interactions between a certain proposed project and other current and future projects are presented in Box 19.

- Examples of the possible interactions between a certain proposed project and other current and future projects

Possible interactions between current and future projects that can conduct to cumulative effects

Effects of other projects at construction phase and effects of the proposed project during its construction phase

Effects of other projects at construction phase and effects of the proposed project during its operation phase

Effects of other projects at operation phase and effects of the proposed project during its construction phase

Effects of other projects at operation phase and effects of the proposed project during its operation phase

Some examples of possible cumulative effects occurrence by implementation of projects concerning water and waste water infrastructure are given below:

  - noise through construction activities (equipment) and noise through traffic increasing negative effects on fauna, human beings, material assets (as tourism in the area);

  - changes of the receiving water body characteristics through increased loads of pollutants from the WWTP effluent discharges and groundwater pollution by infiltration of leaks as a result of damages occurrence to civil structures, platforms, pipes etc. at the WWTP location increasing negative effects on surface water bodies, aquatic flora and fauna of the receiving water body, material assets (water use downstream WWTP location – recreational, fisheries, water supply);

  - soil erosion through removal of vegetation and increased turbidity on surface water body through water runoff from a sloped area, and affecting water habitat of fauna species;

  - reduction of flows to river the receiving the WWTP effluent, for example, through water diversions required by hydro-technical works located upstream the WWTP outlet, and increased loads of pollutants from the WWTP effluent discharges;

  - current or planned waste water treatment facilities and effluents discharged into a river from the same river catchment’s area – there can be identified cumulative impacts due surplus of effluent nutrients or biosolids.

## Risks cases

This section of the EIA Report will identify the project activities that may result in incidents with significant impact on the environment; also, consequences of possible natural hazards would be addressed here.

Typical risk cases that may need to be considered are:

- seismic activity;

- landslides;

- floods;

- fire;

- incidents related to toxic or dangerous chemicals;

- occupational health and safety incidents;

- possible hazards originating from neighbouring industrial areas.

- Data to be provided with regard to risk cases

Seismic activity

Data regarding seismic occurrences in the region;

Design long-term structures at the site to the appropriate Seismic Zone;

Identification of any affected areas during such an event, for example failure of water supply pipelines;

Mitigation measures for seismic event.

Landslides

Identification of areas prone to landslides in the project area;

Identification of the main effects in the case of landslides and consequently the area affected, and their impact on the affected area;

Identification of works and equipment that can be affected, according to each project component;

Prevention and mitigation measures.

Flooding

Identification of the floods pathways;

Identification of areas exposed to flooding;

Identification of the main effects in the case of flooding of exposed areas, for example damages and blockage of sewer pipes;

Prevention and mitigation measures.

Fire

Causes of fire hazard, e.g. during the construction phase: spontaneous combustion of stockpiled waste; during the operation phase: accidental methane release to air because of the failure of digestion tanks;

Possible effects on project works/activity;

Fire prevention and control measures.

Incidents related to hazardous substances

Dangerous substances used;

Identification of possible incidents involving dangerous substances, e.g. those related to storage and handing chemicals;

Prevention and mitigation measures.

Occupational health and safety incidents

Occupational health and safety incidents, e.g. during the construction phase: working in confined spaces; during the operation phase: workers exposed to gas emissions which can cause health effects;

Prevention and mitigation measures.

Possible hazards coming from neighbouring industrial areas

Identification of industrial areas, in the vicinity or within project area, which can pose a hazard threat to the project works/activity;

Identification of the hazard threats and possible effects on the project works/activity;

Prevention and mitigation measures.

# Environmental Monitoring Programme

Environmental monitoring is a key issue to be covered in the EIA Report. Although under Bulgarian national legislation there is no specific requirement for preparation of such a plan, this is considered as a good practice. Hence, the monitoring measures are discussed in relation to mitigation of the significant environmental impacts and are included in the plan for implementation of the mitigation measures. The EIA reports consistently recommend the preparation of a self-monitoring plan to be implemented during each phase of the project implementation.

It is recommended the EIA Report to contain a monitoring programme, both for the construction and operation phase, having the following objectives:

    - compliance of the effective current situation with the main EIA conclusions;

    - variation of certain parameters (as identified in the EIA Report) for the main environmental factors and compliance with the environmental standards;

    - assessment the effectiveness of the implemented mitigation measures;

    - establishment of a database for the above mentioned  measures;

    - compliance with relevant legislation/ standards, the Water Permit or the requirements of the EIA Decision

The monitoring programme can include:

      - Programme of monitoring the implementation of the measures for prevention or mitigation of the adverse environmental effects;

An example regarding the provision of data regarding a summary of the predicted negative impacts associated with the project and corresponding mitigation measures, and responsibilities for their implementation, is given in Box 21 (it can be used also, as a checklist, on periodically inspections);

      - Programme of sampling and specific analyses for assessing project discharges (to air, surface and groundwater, soil, solid waste, noise), and checking the compliance with the environmental standards (an example regarding such a programme is given in Box 22). This programme will cover aspects related to the following:

- emissions of pollutants (to air, to water, to soil, etc.);

- for each parameter: the sampling locations/points, number of tests/samples, sampling frequency) should be indicated;

- generation of waste (types, quantities);

- institutional capacity to implement the monitoring programme;

- format and frequency of reporting.

- Programme for monitoring the implementation of the measures for prevention and/or mitigation the adverse environmental effects - non-exhaustive, for illustrative purposes only

| Environmental Factors | Environmental adverse effects | Preventive/ Mitigation measure | Responsibility | Comments |
| --- | --- | --- | --- | --- |
| Design phase |
| Surface water | Pollution through discharge of non-compliant quality effluent | Appropriate waste water treatment technique, according to the quality parameters requirements of the receiver river body | Design Team |  |
| Groundwater | Pollution due to infiltration of waste water caused by damages to waste water collector - blockages | Considering the discharges from individual sources and the cumulative discharge of the entire project as to ensure and maintain maximum depth of flow and its corresponding velocity. | Design Team |  |
| Human beings | Odour generated by the WWPS and WWTP operation | Development of buffer zones around the WWPS and WWTP sites; Odour control techniques included in the project design. | Design Team |  |
| Material assets | Noise and vibration | Include noise and vibration mitigation measures in the project design | Design Team |  |
| Soil | Pollution through infiltrations of the leachate from the temporary storage location of the sludge resulted from waste water treatment | Compliance with the construction requirements for the sludge storage location, especially related to water impermeable basis | Design Team - requirement for the Contractor |  |
| Construction phase |
| Air | Pollution with dust produced during earthworks | Prevention of dust through sprinkling during periods of dry weather; Daily cleaning of the access ways in the neighbourhood of the construction yard and working sites. | Contractor |  |
|  | Pollution through air pollutants emissions from motor vehicles, transport and construction motor equipment | Regular inspections of the vehicles and equipment; Limitation of working hours for the works located in sensitive locations. | Contractor | Frequency of inspections |
| Surface water | Pollution due to the discharges into river of domestic or industrial waste water from construction yard or from working sites; | Waste water treatment corresponding to the quality category of the receiving water body (temporary sanitary facilities - portable chemical toilet, oil separator or grease trap); Periodical control and proper maintenance of waste water treatment units. | Contractor | In place at commissioning of works |
| Groundwater | Pollution through rain water runoff or infiltration of accidental spills (e.g. fuel and lubricants, dangerous substances) as a result of improper storage facilities | Storage fuels, lubricants and chemicals in appropriate storage facilities (restricted access, sealed packages); Fuelling of vehicles and equipment done at workshops/sites with adequate leakage prevention (e.g. impermeable surface, settlers and oil separator). | Contractor | In place at commissioning of works |
| Soil | Soil erosion (especially in sloping areas), as a result of excavation works (at the working area along pipelines routes or at the locations of civil structures) | Restriction of major earthworks in the dry period; Execution of silt screens; Working site drainage to facilitate run-off discharge and, if possible, treatment (sedimentation) for reducing silt loading; Re-vegetation programme. | Contractor | It will be specified: restriction period; locations where works are needed, works type; schedule of revegetation programme. |
| Surface and Groundwater | Pollution through rain water runoff or infiltration of accidental spills (e.g. fuel and lubricants, dangerous substances) as result of improper storage facilities | Storage fuels, lubricants and chemicals in appropriate storage facilities (restricted access, sealed packages); Fuelling of vehicles and equipment done at workshops/sites with adequate leakage prevention (e.g. impermeable surface, settlers and oil separator). | Contractor | In place at commissioning of works |
| Operation phase |
| Surface water | Pollution through discharge into the receiving water body of non-compliant quality effluent as a result of incomplete waste water treatment, which can be caused by a failure of electric supply, or of electrical and mechanical equipment | Emergency backup power; Back‐up equipment; Develop and implement a preventive maintenance programme, emergency operational plan, inspection procedures, etc. Regular inspections to timely detect any failures, and take appropriate remedial action. | Operator | In place at commissioning of works; Frequency of inspections. |
| Air | Odour because of inappropriate maintenance operations or because of some dysfunctions occurrence of WWCS; Odour due to inappropriate maintenance operations or any other dysfunction. | Regular inspections; Provision of backup equipment for WWPS; Prevent sludge accumulation on waste water networks (by flushing with fresh water); De-clogging operations on waste water network. | Operator | Frequency of inspections |
| Air | Odour because of deficient operation of the WWTP | Monitoring the operation of the WWTP in order to optimize the treatment process and avoid expel of odours; Implementation of procedures for odour abatement measures, e.g. : minimisation of the time for sludge retention in primary settlement, applying of extended aeration to avoid primary settlement. | Operator |  |
| Decommissioning phase |
| Surface, groundwater, air …soil | The adverse effects are usually similar to those predicted for the construction phase | Similar to those recommended for the construction phase | Contractor (involved in decommissioning activities) |  |
| Soil | Pollution of the WWTP site because of damages to basins, platforms, pipes etc. during the WWTP operation | Carry out detailed study to establish pollution extent (area, depth) and recommendations for corresponding remediation actions | Developer/Operator |  |

- Programme of sampling and specific analyses for assessing project discharges (to air, water and groundwater, soil, solid waste, noise) and checking the compliance with the environmental standards – not exhaustive, for illustrative purposes only

CONSTRUCTION PHASE

Air quality in the vicinity of construction sites, especially those regarding sensitive receptors locations, e.g. dust and emissions from motor vehicles, transport and construction motor equipment; Noise level due to traffic, construction equipment, and construction activities; measurements in the vicinity of the construction yard, works sites; Surface and groundwater (upstream and downstream the construction yard), e.g. dissolved oxygen, turbidity and/or suspended solids, oil grease, etc.. For each parameter the sampling locations/points, number of tests/ samples, sampling frequency will be indicated.

Rehabilitation/extension and/or demolition of an existing WWTP

Soil sampling from critical areas (soils that can be polluted from leaching of waste water, in particular underneath and around the basins, from spills of lubricants, fuel and other): and specific analyses to determine, for example heavy metals content, residual oil content, nitrogen, etc.; WWTP influent and effluent - quantitative monitoring: flows, volumes; WWTP influent and effluent - qualitative monitoring: physical and chemical parameters, for example: pH, TSS, BOD, COD, TDS; Waste water receiving water body - qualitative monitoring: it is recommended to determine the same physical and chemical parameters as for the WWTP effluent; depending on the water body sensitivity and other parameters can be required (e.g. bacteriological parameters). For each parameter the sampling locations/points, number of tests/ samples, sampling frequency will be indicated.

OPERATION PHASE

Waste water quality monitoring related to waste water treatment : Influent waste water quantitative parameters: waste water flows (m³/hour; m³/day, m³/year); Influent waste water qualitative parameters - specific analyses, e.g.: pH, TSS, BOD, COD, TKN, P, TDS, other parameters depending on the activities developed in the area of the WWCS, such as heavy metals, phenol, detergent, oil products etc.; Waste water qualitative parameters within different waste water treatment stages for checking the efficiency of the treatment process and, in the case of failure, application of corrective measures, as dosage of chemicals, additional aeration, etc.( pH, TSS, BOD, COD, the BOD/COD ratio for biological treatment characterization, dissolved oxygen and NO3 in aeration basins). Generally, a WWTP is equipped with data collecting systems, which is used for monitoring, automatic control, and as a decision base for operational strategies. WWTP effluent qualitative parameters as result of specific analyses (e.g. pH, TSS, BOD, COD, TKN, P, TDS, other parameters required by the receiver water body sensitivity as bacteriological parameters); The sampling frequency, the number of samples and concerned analyses depends on the capacity of the WWTP, and the potential impact of the water discharged into the receiving water body. Surface water body receiving the WWTP effluent: qualitative parameters to be monitored should include at least the monitored parameters of the WWTP effluent. It is recommended that the sampling be taken up- and downstream of the WWTP outlet. Waste water quality monitoring on WWCS. Is recommended to check periodically the waste water quality discharged into the sewage network especially the waste water discharged by industries by means of periodical analyses of samples taken from control points - located upstream the discharge into sewage collector). Monitoring of water consumption; Monitoring of the sludge resulted from waste water treatment: Quantitative and qualitative monitoring related to the sludge resulted from different stages of the waste water treatment process: raw sludge, biological process sludge, and surplus/waste sludge; Parameters to be monitored as part of the process control include the mineralization rate, sludge age, organic substances content, humidity (%), dry substance content (%), temperature and pH; Qualitative monitoring of the treated sludge considering its final destination: analyses to determine pollutants content, as heavy metals, residual oil, coliforms, etc.; Quantitative monitoring: the records of the sludge quantities depending on the disposal options. Air quality monitoring - air quality in vicinity of WWPS, WWTP: e.g. ammonia, hydrogen sulphide; Noise monitoring – the measurements of noise levels will be conducted in the vicinity of the WPSs, WWPSs, and WWTP. The frequency of the measurements depends on the location sensitivity in the works vicinity (residential area, recreational area, hospitals, etc.). For each parameter the sampling locations/points, number of tests/ samples, sampling frequency will be indicated.

Monitoring programme of materials and chemical substances used in waste water treatment process

Records of type and quantities used; Operational processes which involve use of materials and chemical substances ; Storage location and facilities; Storage and handling procedures.

Monitoring programme of waste

Types and quantities of waste generated; Storage facilities; Final destination of the waste (reuse, recycling/recovery, landfill, incineration).

# Non-Technical Summary

The submission of a non-technical summary (NTS) of the information contained in the EIA Report is a legal requirement of the EIA Directive (Article 5), respectively under Article 96(1)(9) of the LEP Article 12(1)(5) of the EIA Ordinance. It should be reminded that the NTS is defined in point 27 of the Additional Provisions to the LEP as “a brief presentation of the information in the EIA statement in a language comprehensible to the general public of a length not less than 10 per cent of the length of the statement and containing the requisite visuals (maps, photographs, charts)”. Pursuant to Article 12(1)(5) of the EIA Ordinance the NTS is a self-standing document presented as an annex to the EIA report.

The NTS should enable the public to gain appreciation of the project, to understand its likely significant impacts and the mitigation measures that are being proposed by the developer. The NTS may be available as a separate document and should be clear in its content, structure and language. Rather than copying and pasting entire sections from the EIA Report the text of the NTS should be re-phrased and generally be written in a non-technical language that is understandable for the general public and thus avoid scientific or technical jargon.

Overall, the NTS should be a fair reflection of the main EIA Report and cover all aspects of the EIA process. The format should be largely developed along the main headers of the EIA Report, i.e. it should contain a description of the project and its objective, a description of the existing environmental conditions, the likely significant impacts, the proposed mitigation and management measures and any other critical matters. Some information on the development consent process and on the previous stages of the EIA process (i.e. the results of screening, if any, and scoping and public consultations) should also be provided.

Generally, the NTS may be decided to be a stand-alone document and should thus also include a locational map and layout plan of the project. A summary of impacts, mitigation measures and residual impacts may be presented in table format.

- Content of Non-technical summary

Project description

Brief project description

Uncertainties about the project

Significant impacts (positive and negative)

Overview of the approach to the assessment

Uncertainties about environmental effects of project implementation

Data about sequence of EIA procedure stages accomplished so far for the project

Screening Decision (if applicable)

Scoping document (if applicable)

Consultation/opinion of authorities likely to be concerned by the project by the reason of their environmental authorities

Information regarding public consultation

# Challenges in EIA Report preparation

The EIA Report should contain comprehensive but concise information in relation with the main aspects addressed.

An ambiguous description of the technical processes and of the activities related to the project can make it difficult for the reader to understand the EIA approach.

It is recommended to avoid the addition of data and information which is not relevant for the project, for example, about the existing baseline environmental conditions, or a large description of the fauna species in the region for a project that is proposed to be implemented in an urban area.

During the EIA, some difficulties could be encountered, and they refer to the following:

- uncertainty about some information regarding baseline environmental conditions;

- limited data regarding construction phase of the project;

- possible changes of land development planning, fact which can require a re-evaluation of the basic data for the project design;

- lack of guidelines/methodologies for the assessment of the environmental impact significance.

Where appropriate, the difficulties encountered during the EIA will be mentioned in the EIA Report, and the uncertainty of impact prediction it will be specified also.

If complete information cannot be provided, it must be made clear that, the information is not intentionally withheld and that all parties will be aware of the incompleteness. The resultant decision would be either qualified or conditional.

Bulgarian national legislation in Article 96(1)(10) of the LEP reads that the EIA report should contain information on the difficulties (technical reasons, insufficiency or lack of data) encountered in the collection of information for preparation of the EIA Report.

# Environmental Management Plan

The implementation of impact mitigation and monitoring of impacts often represent the weak links in the EIA process. A best practice approach to face this problem is to prepare an Environmental Management Plan (EMP), a tool designed to ensure continuity between project planning / appraisal, detailed design, implementation / construction and operation / maintenance.

The preparation of an EMP is not formally required under the provisions of the EIA Directive or of the Bulgarian national law. Internationally, however, the EMP is considered as best practice to ensure that commitments given at the planning and assessment stage will be carried through to the construction and/or operation stage of the project. As the project is developed to further detail, the EMP will usually be refined including adjustments to the terms and conditions specified in any project approval. This good practice to a large extent is implemented in Bulgaria. As it was already mentioned, the plan for implementation of the mitigation measures, required under the LEP and the EIA Ordinance, logically includes measures for monitoring of the impacts. This plan is endorsed by the competent authority with the positive EIA decision. Moreover, in compliance with Article 99(1)(6) and (8) of the LEP, the EIA decision contains “conditions for implementation, including measures to prevent, reduce or offset significant adverse effects on the environment, as well as deadlines for compliance, where necessary”. These conditions are then subject to control (Chapter IX of the LEP).

The key objectives of an EMP are

- To ensure compliance of project execution with the applicable environmental legislation (local, national, EU or international);

- To ensure that technical and organizational resources will be mobilized to implement the necessary mitigation measures;

- To provide a reference for impact management, environmental performance monitoring and identification of any changes and unforeseen events during project implementation, which may not have been considered in the EIA.

The EMP is developed based on the results of the EIA, i.e. the anticipated environmental impacts and proposed mitigation measures. Usually, an EMP is set up after an EIA has been conducted, often as a requirement of the development consent drafted by the lead environmental authority. Some of the issues addressed in the EMP would be followed-up during the detailed design, but the bulk of the measures usually relates to construction and the operational stage of the project.

Generally, when an EMP is requested by funding institutions or authorities, it should be developed before the related activities are undertaken. The EMP is a document that should be the made available to contractors (construction and operation companies) since the bidding phase. The mitigation measures should be known and budgeted by the bidders being a part of the contractual conditions. Furthermore, the EMP must be completely operational as soon as the construction stage starts.

An EMP will present a summary of the significant impacts that are likely to occur and setting out the approach to be taken by the developer to safeguard all environmental interests during construction and operation and in line with the applicable legislation.

For an EMP that is submitted as a separate document the contents may be as shown in Box 24.

- Components of EMP

Details of developer /operator/contractor:

Name and address; Staff numbers; Company structure (organization chart is recommended); Site address (details will be provided for all areas where the company is operating).

Overview of the proposed activity:

Brief description of the project: buildings and civil structures, equipment and installations and corresponding operational activities; Brief description of the construction yard, construction activities and ancillary works, construction techniques, schedule of construction activities on different locations (if it is the case).

Description of project location

Summary of the critical activities causing impacts of medium to high significance

Relevant legal requirements and standards that apply to the project

Regulatory documents – legal agreements, consents and permits (already granted or have to apply for) – as regard construction and operation phase of the project:

Specifications related to the provisions of the regulatory documents: e.g. key conditions: performance specifications; Environmental monitoring required by regulatory documents .

Environmental Monitoring Programme – see Chapter 7

Risk cases - see Subsection 6.5.

Schedule for EMP implementation and reporting - showing the sequence and timing (including frequency and duration) of the management and monitoring activities of the EMP

Maps, diagrams and charts (as indicated in Chapter 3 - Project description)

# References

- EIA Guidance manual for building, construction, townships and area development projects (Ministry of Environment & Forests - INDIA 2010),http://environmentclearance.nic.in/writereaddata/Form-1A/HomeLinks/building-construction_may-10.pdf

- EIA Guidelines for municipal waste water treatment works (SEAM Project, Egyptian Environmental Affairs Agency, Entec UK Ltd - 2005) http:/www.eeaa.gov.eg/Arabic/main/guides/waste_main1.pdf

- Guidelines for the assessment of indirect and cumulative impacts and impact interactions (EC DG XI Environment, Nuclear Safety & Civil Protection -1999)

- http://ec.europa.eu/environment/eia/eia-studies-and-reports/guidel.pdf

- EIA Guidelines for assessment of urban development (Egyptian Environmental Affairs Agency - 2005) http://www.eeaa.gov.eg/arabic/main/guides/Urban-En.pdf

- Sectorial EIA Guidelines – Waste Water Treatment Plant (Environmental Management Strengthening former Yugoslav Republic of  Macedonia), http://www.zeleni.org.mk/uploads/media/Sektorska_OVZS_- _Precistitelni_stanici_za_otpadni_vodi.pdf

- Sectoral EIA Guidelines Waste water Treatment Plants and Waste water Collection Systems (JASPERS - 2010)  http://www.jaspers-europa-info.org/attachments/129_JASPERS_EIA_Guidelines_2010_WASTEWATER.pdf

- Sectoral EIA Guidelines Groundwater Abstraction and Water Supply Systems (JASPERS - 2010) 	http://www.jaspers-europa-info.org/attachments/129_JASPERS_EIA_Guidelines_2010_WATER_SUPPLY.pdf

- Code of Practice on Odour Nuisance from Sewage Treatment Works (Department for Environment, Food and Rural Affairs, UK – 2006)

- www.defra.gov.uk

- Environmental Impact Assessment and Strategic Environmental Assessment: Towards an Integrated Approach (UNEP - 2004)

- http://www.unep.ch/etu/publications/textONUbr.pdf

- Environmental Impact Assessment: A guide to good practice and procedures (Department for Communities and Local Government, London UK - 2006)

- www.communities.gov.uk

- Guideline for Environmental Management Plans (CSIR Report No ENV-S-C 2005-053 H. Republic of South Africa, Provincial Government of the Western Cape, Department of Environmental Affairs & Development Planning, Cape Town).

# Annexes

ANNEX 1

EU environmental legislation most relevant to the guidelines

- Council Directive 91/271/EEC of 21 May 1991 concerning urban waste water treatment, as amended

- Directive 2000/60/EC of the European Parliament and of the Council of 23 October 2000 establishing a framework for Community action in the field of water policy, as amended

- Directive 2001/42/EC of the European Parliament and of the Council of 27 June 2001 on the assessment of the effects of certain plans and programmes on the environment

- Directive 2011/92/EU of the European Parliament and of the Council of 13 December 2011 on the assessment of the effects of certain public and private projects on the environment

- Council Directive 92/43/EEC of 21 May 1992 on the conservation of natural habitats and of wild fauna and flora, amended

- Directive 2008/50/EC of the European Parliament and of the Council of 21 May 2008 on ambient air quality and cleaner air for Europe

- Directive 2002/49/EC of the European Parliament and of the Council of 25 June 2002 relating to the assessment and management of environmental noise

- Council Directive 70/157/EEC of 6 February 1970 on the approximation of the laws of the Member States relating to the permissible sound level and the exhaust system of motor vehicles, as amended

- Directive 2008/98/EC of the European Parliament and of the Council of 19 November 2008 on waste and repealing certain Directives

- Directive 2003/4/EC of the European Parliament and of the Council of 28 January 2003 on public access to environmental information and repealing Council Directive 90/313/EEC

REMARK: Special attention should be paid to the expected amendment of EIA Directive.

ANNEX 2

BULGARIAN LEGISLATION RELEVANT to the guidelines

| TITLE OF THE LEGAL ACT IN ENGLISH LANGUAGE | TITLE OF THE LEGAL ACT IN BULGARIAN LANGUAGE |
| --- | --- |
| LAWS | ЗАКОНИ |
| Law on Spatial Development (SG 1 of 02/01/2001, as last amended and supplemented SG 28 of 19/03/2013) | Закон за устройство на територията, (обн., ДВ, бр. 1 от 02.01.2001 г., посл. изм. и доп., ДВ, бр. 28 от 19.03.2013 г.) |
| Law on Black Sea Coast Development (SG 48 of 15/06/2007, as last amended SG 28 of 19/03/2013) | Закон за устройството на Черноморското крайбрежие (обн., ДВ, бр. 48 от 15.06.2007 г., посл. изм. ДВ, бр. 28 от 19.03.2013 г.) |
| Law on Environmental Protection (SG 91 of 25/09/2002, as last amended and supplemented SG 27 of 15/03/2013) | Закон за опазване на околната среда, (обн., ДВ, бр. 91 от 25.09.2002 г., посл. изм. и доп., ДВ, бр. 27 от 15.03.2013 г.) |
| Law on Clean Ambient Air (SG 45 of 28/05/1996, as last amended SG 102 of 21/12/2012) | Закон за чистотата на атмосферния въздух, (обн., ДВ, бр. 45 от 28.05.1996 г., посл. изм. ДВ бр. 102 от 21.12.2012 г.) |
| Law on Waste Management (SG 53 of 13/07/2012) | Закон за управление на отпадъците (обн., ДВ, бр. 53 от 13.07.2012 г.,) |
| Law on Soils (SG 89 of 06/11/2007, as last amended SG 92 of 22/11/2011) | Закон за почвите (обн., ДВ. бр. 89 от 06.11.2007 г., посл. изм. ДВ, бр. 92 от 22.11.2011 г.) |
| Law on the liability for prevention and remediation of environmental damages (SG 43 of 29/04/2008, as last amended SG 53 of 13/07/2012) | Закон за отговорността за предотвратяване и отстраняване на екологични щети (oбн., ДВ, бр. 43 от 29.04.2008 г., посл. изм. ДВ, бр. 53 от 13.07.2012 г.) |
| Law on Biological Diversity (SG 77 of 09/08/2002, as last amended and supplemented SG 27 of 15/03/2013) | Закон за биологичното разнообразие (обн., ДВ, бр. 77 от 09.08.2002 г., посл. изм. и доп. ДВ, бр. 27 от 15.03.2013 г.) |
| Law on Protected Areas (SG 133 of 11/11/1998, as last amended SG 27 of 15/03/2013) | Закон за защитените територии (обн. ДВ, бр. 133 от 11.11.1998 г., посл. изм. ДВ, бр. 27 от 15.03.2013 г.) |
| Law on Protection of Animals (SG 13 of 08/02/2008, as last amended and supplemented SG 92 of 22/11/2011) | Закон за защита на животните (обн., ДВ, бр. 13 от 08.02.2008 г., посл. изм. и доп. ДВ, бр. 92 от 22.11.2011 г.) |
| Law on Protection of Plants (SG 91 of 10/10/1997, as last amended and supplemented SG 28 of 05/04/2011) | Закон за защита на растенията (обн., ДВ, бр. 91 от 10.10.1997 г., посл. изм. и доп. ДВ, бр. 28 от 05.04.2011 г.) |
| Law on Waters (SG 67 of 27/07/1999, as last amended SG 82 of 26/10/2012) | Закон за водите (обн., ДВ, бр. 67 от 27.07.1999 г.; посл. изм., ДВ. бр. 82 от 26.10.2012 г.) |
| Law on Protection Against Environmental Noise (SG 74 of 13/09/2005, as last supplemented SG 32 of 24/04/2012) | Закон за защита от шума в околната среда (обн., ДВ, бр. 74 от 13.09.2005 г., посл. доп. ДВ, бр. 32 от 24.04.2012 г.) |
| Law on Protection Against the Harmful Impact of Chemical Substances and Mixtures(title amended SG 114/2003, SG No. 63/2010, effective 13.08.2010, promulgated SG 10 of 04/02/2000, as last amended and supplemented SG 84 of 02/11/2012) | Закон за защита от вредното въздействие на химичните вещества и смеси (загл. изм. ДВ, бр. 114 от 2003 г., бр. 63 от 2010 г., в сила от 13.08.2010 г., обн., ДВ, бр. 10 от 04.02.2000 г., посл. изм. и доп., бр. 84 от 02.11.2012 г.) |
| Law on Access to Spatial Data (SG 19 of 09/03/2010) | Закон за достъп до пространствени данни (обн., ДВ, бр. 19 от 09.03.2010 г.) |
| Law on Protection of Agricultural Lands (SG 35 of 24/04/1996,) | Закон за опазване на земеделските земи (обн., ДВ, бр. 35 от 24.04.1996 г, посл. изм., ДВ, бр. 27 от 15.03.2013 г.) |
| Law on Health (SG 70 of 10/08/2004, as last amended SG 30 of 26/03/2013) | Закон за здравето (обн., ДВ, бр. 70 от 10.08.2004 г., посл. изм. ДВ, бр. 30 от 26.03.2013 г., в сила от 1.01.2014 г.); |
| Law on Disaster Protection (SG 102 of 19/12/2006, as last amended and supplemented SG 80 of 14/10/2011) | Закон за защита при бедствия (обн., ДВ, бр. 102 от 19.12.2006 г., посл. изм. и доп. бр. 80 от 14.10.2011 г.); |
| Law on Health and Safety Labour Conditions (SG 124 of 23/12/1997, as last amended SG 15 of 15/02/2013) | Закон за здравословни и безопасни условия на труд (обн., ДВ, бр. 124 от 23.12.1997 г., посл. изм. ДВ, бр. 15 от 15.02.2013 г.) |
| Law on Concessions (SG 36 of 02/05/2006, as last amended and supplemented SG 24 of 12/03/2013) | Закон за концесиите (обн., ДВ, бр. 36 от 02.05.2006 г., посл. изм. и доп. ДВ, бр. 24 от 12.03.2013 г.) |
| Law Cultural Heritage (SG 19 of 13/03/2009, as last amended and supplemented SG 15 of 15/02/2013, in force as of 01/01/2014) | Закон за културното наследство (обн., ДВ, бр. 19 от 13.03.2009 г., посл. изм., ДВ. 15 от 15.02.2013 г., в сила от 01.01.2014 г.) |
| Law on Access to Public Information (SG 55 of 07/07/2000, as last amended SG 39 of 20/05/2011) | Закон за достъп до обществена информация (обн., ДВ, бр. 55 от 07.07.2000 г., посл. изм., ДВ, бр. 39 от 20.05.2011 г.) |
| Law on Geodesy and Cartography (SG 29 of 07/04/2006, as last amended SG 77 of 09/10/2012) | Закон за геодезията и картографията (обн., ДВ, бр. 29 от 07.04.2006 г., посл. изм., ДВ, бр. 77 от 09.10.2012 г.) |
| Law on Cadastre and the Property Register (SG 34 of 25/04/2000, as last amended SG 15 of 15/02/2013, in force as of 01/01/2014) | Закон за кадастъра и имотния регистър (обн., ДВ, бр. 34 от 25.04.2000 г., посл. изм., ДВ, бр. 15 от 15.02.2013 г., в сила от 1.01.2014 г.) |
| Law on Ratification of the Convention on Environmental Impact Assessment in a Transboundary Context (SG 28 of 28/03/1995) | Закон за ратифициране на Конвенцията за оценка на въздействието върху околната среда в трансграничен контекст (обн., ДВ, бр. 28 от 28.03.1995 г.) |
| Law on Ratification of the Convention on Access to Information, Public Participation in Decision-making and Access to Justice in Environmental Matters (SG 91 of 14/10/2003) | Закон за ратифициране на Конвенцията за достъпа до информация, участието на обществеността в процеса на вземането на решения и достъпа до правосъдие по въпроси на околната среда (обн., ДВ, бр. 91 от 14.10.2003 г.) |
| ORDINANCES | НАРЕДБИ |
| Ordinance on the conditions and the order for implementing environmental impact assessment (adopted by Council of Ministers Decree (CMD) No. 59 of 07/03/2003, prom. SG 25 of 18/03/3003, as last amended and supplemented SG 94 of 30/11/2012) | Наредба за условията и реда за извършване на оценка на въздействието върху околната среда (загл. изм. ДВ, бр. 3 от 2006 г., приета с ПМС № 59 от 07.03.2003 г., обн., ДВ, бр. 25 от 18.03.2003 г., посл. изм. и доп. ДВ, бр. 94 от 30.11.2012 г.) |
| Ordinance on the conditions and the order for implementing environmental assessment of plans and programmes (adopted by CMD No. 139 of 24/06/2004, prom. SG 57 of 02/07/2004, as last amended and supplemented SG 94 of 30/11/2012) | Наредба за условията и реда за извършване на екологична оценка на планове и програми (загл. изм. ДВ, бр. 3 от 2006 г., приета с ПМС № 139 от 24.06.2004 г., обн., ДВ, бр. 57 от 02.07.2004 г., посл. изм. и доп. ДВ, бр. 94 от 30.11.2012 г.) |
| Ordinance on the development of management plans for protected areas (adopted by CMD No. 7 of 08/02/2000, prom. SG 13 of 15/02/2000, as amended and supplemented SG 55 of 20/07/2012) | Наредба за разработване на планове за управление на защитени територии (приета с ПМС № 7 от 08.02.2000 г., обн., ДВ, бр. 13 от 15.02.2000 г., изм. и доп., ДВ,бр. 55 от 20.07.2012 г.) |
| Ordinance No. 2 of 18/12/2006 on the conditions and the procedure for the establishment and the functioning of the National System for Monitoring of the Status of the Biological Diversity (SG 3 of 12/01/2007) | Наредба № 2 от 18.12.2006 г. за условията и реда за създаването и функционирането на Националната система за мониторинг на състоянието на биологичното разнообразие (обн., ДВ, бр. 3 от 12.01.2007 г.) |
| Ordinance No. 5 of 01/08/2003 on the conditions and the procedure for preparation of action plans for plant and animal species (SG 73 of 19/08/2003) | Наредба № 5 от 01.08.2003 г. за условията и реда за разработване на планове за действие за растителни и животински видове (обн., ДВ, бр. 73 от 19.08.2003 г.) |
| Ordinance on the conditions and order for carrying out compatibility assessment on plans, programmes, projects and investment proposals with the conservation objectives of the protected areas (adopted by a Council of Minister Decree No. 201 of 31/08/2007, prom. SG 73 of 11/09/2007, as last amended and supplemented SG 94 of 30/11/2012) | Наредба за условията и реда за извършване на оценка за съвместимостта на планове, програми, проекти и инвестиционни предложения с предмета и целите на опазване на защитените зони (приета с ПМС № 201 от 31.08.2007 г., обн., ДВ, бр. 73 от 11.09.2007 г., в сила от 11.09.2007 г., посл. изм. и доп. ДВ, бр. 94 от 30.11.2012 г.) |
| Ordinance No. 19 of 25/10/2012 on construction on agricultural lands without changing its purpose of use (SG 85 of 06/11/2012) | Наредба № 19 от 25.10.2012 г. за строителство в земеделските земи без промяна на предназначението им (обн., ДВ, бр. 85 от 06.11.2012 г.) |
| Ordinance No. 1 on exploration, use and protection of groundwater (SG 87 of 30/10/2007, as last amended and supplemented SG 28 of 19/03/2013) | Наредба № 1 за проучване, ползване и опазване на подземните води (обн., ДВ, бр. 87 от 30.10.2007 г., посл. изм. и доп. ДВ, бр. 28 от 19.03.2013 г.) |
| Ordinance No. 3 of 16/10/2000 on the conditions and the procedure for exploration, design and exploitation of sanitary-protection zones around the water sources and facilities and around the mineral water sources used for health treatment, prophylactics, drinking and hygiene needs (SG 88 of 27/10/2000) | Наредба № 3 от 16.10.2000 г. за условията и реда за проучване, проектиране, утвърждаване и експлоатация на санитарно-охранителните зони около водоизточниците и съоръженията за питейно-битово водоснабдяване и около водоизточниците на минерални води, използвани за лечебни, профилактични, питейни и хигиенни нужди (обн., ДВ, бр. 88 от 27.10.2000 г.) |
| Ordinance No. 2 of 08/06/2011 on the issuing of permits for the discharge of waste waters in water bodies and setting individual emission restrictions to point pollution sources (SG 47 of 21/06/2011, as amended SG 14 of 17/02/2012) | Наредба № 2 от 8.06.2011 г. за издаване на разрешителни за заустване на отпадъчни води във водни обекти и определяне на индивидуалните емисионни ограничения на точкови източници на замърсяване (обн., ДВ, бр. 47 от 21.06.2011 г., изм., бр. 14 от 17.02.2012 г.) |
| Ordinance No. 5 of 30/05/2008 on the management of bathing waters quality (SG 53 of 10/06/2008, as last amended and supplemented SG 5 of 18/01/2013) | Наредба № 5 от 30.05.2008 г. за управление качеството на водите за къпане (обн., ДВ, бр. 53 от 10.06.2008 г., посл. изм. и доп., бр. 5 от 18.01.2013 г.) |
| Ordinance No. 4 of 20/10/2000 on the quality of water intended for fishery and breeding of shellfish organisms (SG 88 of 27/10/2000) | Наредба № 4 от 20.10.2000 г. за качеството на водите за рибовъдство и за развъждане на черупкови организми (обн., ДВ, бр. 88 от 27.10.2000 г.) |
| Ordinance No. 18 of 27/05/2009 on the quality of waters used for irrigation for agricultural products (SG 43 of 09/06/2009) | Наредба № 18 от 27.05.2009 г. за качеството на водите за напояване на земеделските култури (обн., ДВ, бр. 43 от 09.06.2009 г.) |
| Ordinance No. 1 on monitoring of waters (SG 34 of 29/04/2011, as amended and supplemented SG 22 of 05/03/2013) | Наредба № 1 от 11.04.2011 г. за мониторинг на водите (обн., ДВ, бр. 34 от 29.04.2011 г., изм. и доп., бр. ДВ, 22 от 05.03.2013 г.) |
| Ordinance No. 12 on the requirements to the quality of surface waters intended for drinking and human consumption supply (SG 63 of 28/06/2002, as amended SG 15 of 21/02/2012) | Наредба № 12 от 18.06.2002 г. за качествените изисквания към повърхностни води, предназначени за питейно-битово водоснабдяване (обн., ДВ, бр. 63 от 28.06.2002 г., изм. ДВ, бр. 15 от 21.02.2012 г.) |
| Ordinance No. 6 of 09/11/2000 on the emission values of admissible content of harmful and dangerous substances in waste waters discharged in water bodies (SG 97 of 28/11/2000 as amended and supplemented SG 24 of 23/03/2004) | Наредба № 6 от 09.11.2000 г. за емисионни норми за допустимото съдържание на вредни и опасни вещества в отпадъчните води, зауствани във водни обекти (обн., ДВ, бр. 97 от 28.11.2000 г., изм. и доп., бр. 24 от 23.03.2004 г.) |
| Ordinance No. 7 of 14/11/2000 on the conditions and the procedure for discharge of industrial waste waters in the settlements sewerage systems (SG 98 of 01/12/2000) | Наредба № 7 от 14.11.2000 г. за условията и реда за заустване на производствени отпадъчни води в канализационните системи на населените места (обн., ДВ, бр. 98 от 01.12.2000 г.) |
| Ordinance No. N-4 of 14/09/2012 on the characterization of surface waters (SG 22 of 05/03/2013) | Наредба № Н-4 от 14.09.2012 г. за характеризиране на повърхностните води (обн., ДВ, бр. 22 от 05.03.2013 г.) |
| Ordinance No. 2 of 13/09/2007 for protection of waters with nitrates from agricultural sources (SG 27 of 11/03/2008, as amended and supplemented SG 97 of 09/12/2011) | НАРЕДБА № 2 от 13.09.2007 г. за опазване на водите от замърсяване с нитрати от земеделски източници (обн., ДВ, бр. 27 от 11.03.2008 г., изм. и доп., ДВ, бр. 97 от 09.12.2011 г.) |
| Ordinance No. 12 of 15/07/2010 on the norms for sulphur dioxide, nitrogene, particulate matter, lead, benzene, carbon dioxide and ozone in the ambient air (SG 58 of 30/07/2010) | Наредба № 12 от 15.07.2010 г. за норми за серен диоксид, азотен диоксид, фини прахови частици, олово, бензен, въглероден оксид и озон в атмосферния въздух (обн., ДВ, бр. 58 от 30.07.2010 г.) |
| Ordinance No. 11 of 14/05/2007 on the norm for arsenium, cadmium, nickel and polycyclic aromatic carbon oxides in the ambient air (SG 42 of 29/05/2007) | Наредба № 11 от 14.05.2007 г. за норми за арсен, кадмий, никел и полициклични ароматни въглеводороди в атмосферния въздух (обн., ДВ, бр. 42 от 29.05.2007 г.) |
| Ordinance No. 1 of 27/06/2005 on limit emission values for harmful substances (pollutants) released in the atmosphere by installations and activities with immovable sources of emissions (SG 64 of 05/08/2005) | Наредба № 1 от 27.06.2005 г. за норми за допустими емисии на вредни вещества (замърсители), изпускани в атмосферата от обекти и дейности с неподвижни източници на емисии (обн., ДВ, бр. 64 от 05.08.2005 г.) |
| Ordinance No. 6 on the procedure and the methods for measurement of emission of harmful substances released in the ambient air by immovable sources of emissions (SG 31 of 06/04/1999, as last amended SG 102 of 21/12/2012) | Наредба № 6 от 26.03.1999 г. за реда и начина за измерване на емисиите на вредни вещества, изпускани в атмосферния въздух от обекти с неподвижни източници (обн., ДВ, бр. 31 от 06.04.1999 г., посл. изм., бр. ДВ, 102 от 21.12.2012 г.) |
| Ordinance No. 10 of 24/02/2004 on the conditions and the procedure for approval of the types of internal combustion engines to be installed off-road mobile machinery regarding their emissions of pollutants (SG 28 of 06/04/2004, as last amended and supplemented SG 69 of 11/09/2012) | Наредба № 10 от 24.02.2004 г. за условията и реда за одобрение на типа на двигатели с вътрешно горене за извънпътна техника по отношение на емисиите на замърсители (обн., ДВ, бр. 28 от 06.04.2004 г., посл. изм. и доп. ДВ, бр. 69 от 11.09.2012 г.) |
| Ordinance No. 7 on the assessment and management of the quality of ambient air (SG 45 of 14/05/1999) | Наредба № 7 от 3.05.1999 г. за оценка и управление качеството на атмосферния въздух (обн., ДВ, бр. 45 от 14.05.1999 г.) |
| Ordinance No. 54 of 13/12/2010 on the activities of the national system for monitoring of the environmental noise and the requirements to self-monitoring and submission of information by the industrial sources of environmental noise (SG 3 of 11/01/2011) | Наредба № 54 от 13.12.2010 г. за дейността на националната система за мониторинг на шума в околната среда и за изискванията за провеждане на собствен мониторинг и предоставяне на информация от промишлените източници на шум в околната среда (обн., ДВ, бр. 3 от 11.01.2011 г.) |
| Ordinance No. 6 of 26/06/2006 on the indicators for environmental noise, measuring the level of discomfort during the different parts of the day, the limit values of the indicators for environmental noise, the methods for assessment of the limit values of the indicators for noise and the harmful effects of the noise on the health of the population (SG 58 of 18/07/2006) | Наредба № 6 от 26.06.2006 г. за показателите за шум в околната среда, отчитащи степента на дискомфорт през различните части на денонощието, граничните стойности на показателите за шум в околната среда, методите за оценка на стойностите на показателите за шум и на вредните ефекти от шума върху здравето на населението (обн. ДВ, бр. 58 от 18.07.2006 г.) |
| Ordinance No. 9 of 12/02/2010 on the maximum admissible values of vibrations in the living premises (SG 17 of 02/03/2010) | Наредба № 9 от 12.02.2010 г. за максимално допустимите стойности на вибрациите в жилищни помещения (обн., ДВ, бр. 17 от 02.03.2010 г.) |
| Ordinance No. 9 of 14/03/1991 on the limit permissible levels of electro-magnetic fields in settlements and for the determination of the hygiene-protected areas around emitting sources (SG 35 of 03/05/1991, as last amended and supplemented SG 8 of 22/01/2002) | Наредба № 9 от 14.03.1991 г. за пределно допустими нива на електромагнитни полета в населени територии и определяне на хигиенно-защитни зони около излъчващи обекти (обн., ДВ, бр. 35 от 03.05.1991 г., посл. изм. и доп. ДВ, 8 от 22.01.2002 г.) |
| Ordinance on the prevention of major-accident hazards involving dangerous substances and for limitation of consequences thereto (adopted by CMD No. 238 of 28/09/2012, prom. SG 76 of 05/10/2012) | Наредба за предотвратяване на големи аварии с опасни вещества и за ограничаване на последствията от тях (приета с ПМС № 238 от 28.09.2012 г., обн., ДВ, бр. 76 от 05.10.2012 г.) |
| Ordinance No. 5 of 11/05/1999 on the procedure, methods and periodicity of conducting risk assessment (SG 47 of 21/05/1999) | Наредба № 5 от 11.05.1999 г. за реда, начина и периодичността на извършване на оценка на риска (обн., ДВ, бр. 47 от 21.05.1999 г.) |
| Ordinance No. 2 of 12/09/1990 on protection against accidents in case of activities with dangerous chemical substances (SG 100 of 14/12/1990) | Наредба № 2 от 12.09.1990 г. за защита от аварии при дейности с опасни химически вещества (обн., ДВ, бр. 100 от 14.12.1990 г.) |
| Ordinance on the procedure and the methods for classification, packaging and labelling of chemical substances and mixtures (adopted by CMD No. 182 of 20/08/2010, prom. SG 68 of 31/08/2010) | Наредба за реда и начина на класифициране, опаковане и етикетиране на химични вещества и смеси (приета с ПМС № 182/20.08.2010 г., обн., ДВ, бр. 68 от 31.08.2010 г.) |
| Ordinance No. 3 of 01/08/2008 on the norms for admissible content of dangerous substances in the soils (SG 71 of 12/08/2008) | Наредба № 3 от 01.08.2008 г. за нормите за допустимо съдържание на вредни вещества в почвите (обн., ДВ, бр. 71 от 12.08.2008 г.) |
| Ordinance No. 4 of 12/01/2009 on the soils monitoring (SG 19 of 13/03/2009) | Наредба № 4 от 12.01.2009 г. за мониторинг на почвите (обн., ДВ, бр. 19 от 13.03.2009 г.) |
| Ordinance No. 3 of 01/04/2004 on the classification of waste (SG 44 of 25/05/2004, as amended and supplemented SG 23 of 20/03/2012) | Наредба № 3 от 01.04.2004 г. за класификация на отпадъците (обн., ДВ, бр. 44 от 25.05.2004 г., изм. и доп. ДВ, бр. 23 от 20.03.2012 г.) |
| Ordinance No. 2 of 22/01/2013 on the procedure and the templates for submission of information on the activities with waste, as well as the procedure for maintaining the public registries (SG 10 of 05/02/2013) | Наредба № 2 от 22.01.2013 г. за реда и образците, по които се предоставя информация за дейностите по отпадъците, както и реда за водене на публични регистри (обн., ДВ, бр. 10 от 05.02.2013 г.) |
| Ordinance on the management of construction waste and for the application of recycled construction materials (adopted by CMD No. 277 of 05/11/2012, prom. SG 89 of 13/11/2012) | Наредба за управление на строителните отпадъци и за влагане на рециклирани строителни материали (приета с ПМС № 277 от 05.11.2012 г., обн., ДВ, бр. 89 от 13.11.2012 г.) |
| Ordinance No. 6 of 28/07/2004 on the conditions and the requirements for the construction and exploitation of the installations for incineration and of installations for co-incineration of waste (SG 78 of 07/09/2004, as corrected SG 98 of 05/11/2004) | Наредба № 6 от 28.07.2004 г. за условията и изискванията за изграждането и експлоатацията на инсталации за изгаряне и инсталации за съвместно изгаряне на отпадъци (обн., ДВ, бр. 78 от 07.09.2004 г., попр. ДВ, бр. 98 от 05.11.2004 г.) |
| Ordinance on the requirements to treatment and transport of industrial and hazardous waste (adopted by CMD No. 53 of 19/03/1999, prom. SG 29 of 30/03/1999) | Наредба за изискванията за третиране и транспортиране на производствени и на опасни отпадъци (приета с ПМС № 53 от 19.03.1999 г., обн., ДВ, бр. 29 от 30.03.1999 г.) |
| Ordinance on the procedure and the methods for recovery of sewage sludge from treatment of waste waters by using it in the agriculture (adopted by CMD No. 339 of 14/12/2004, prom. SG 112 of 23/12/2004, as amended and supplemented SG 29 of 08/04/2011) | Наредба за реда и начина за оползотворяване на утайки от пречистването на отпадъчни води чрез употребата им в земеделието (приета с ПМС № 339 от 14.12.2004 г., обн., ДВ, бр. 112 от 23.12.2004 г., изм. и доп. ДВ, бр. 29 от 08.04.2011 г.) |
| Ordinance on the waste oils and waste petrol products (adopted by CMD No. 352 of 27/12/2012, prom. SG 2 of 08/01/2013) | Наредба за отработените масла и отпадъчните нефтопродукти (приета с ПМС № 352 от 27.12.2012 г., обн., ДВ, бр. 2 от 08.01.2013 г.) |
| Ordinance on the end-of live vehicles (adopted by CMD No. 11 of 15/01/2013, prom. SG 2 of 25/01/2013) | Наредба за излезлите от употреба моторни превозни средства (приета с ПМС № 11 от 15.01.2013 г., обн., ДВ, бр. 7 от 25.01.2013 г.) |
| Ordinance No. 3 of 28/02/1987 on the mandatory preliminary and periodic medical checks of workers (SG 16 of 27/02/1987, as last amended and supplemented SG 78 of 30/09/2005) | Наредба № 3 от 28.02.1987 г. за задължителните предварителни и периодични медицински прегледи на работниците (обн., ДВ, бр. 16 от 27.02.1987 г., посл. изм. и доп. ДВ, бр. 78 от 30.09.2005 г.) |
| Ordinance No. 3 of 19/04/2001 on the minimum requirements for the safety and protection of the health of the workers when using personal protection means at their working place (SG 46 of 15/05/2001, as amended and supplemented SG 40 of 18/04/2008) | Наредба № 3 от 19.04.2001 г. за минималните изисквания за безопасност и опазване на здравето на работещите при използване на лични предпазни средства на работното място (обн., ДВ, бр. 46 от 15.05.2001 г., изм. и доп., бр. 40 от 18.04.2008 г.) |
| Ordinance No. 7 of 23/09/1999 on the minimum requirements to the health and safety labour conditions at the working places and when working equipment is used (SG 88 of 08/10/1999, as last amended and supplemented SG 24 of 12/03/2013) | Наредба № 7 от 23.09.1999 г. за минималните изисквания за здравословни и безопасни условия на труд на работните места и при използване на работното оборудване (обн., ДВ, бр. 88 от 08.10.1999 г., посл. изм. и доп. ДВ, бр. 24 от 12.03.2013 г.) |
| Ordinance No. 3 of 25/01/2008 on the conditions and the procedure for the operation of the services for occupational medicine (SG 14 of 12/02/2008) | Наредба № 3 от 25.01.2008 г. за условията и реда за осъществяване дейността на службите по трудова медицина (обн., ДВ, бр. 14 от 12.02.2008 г.) |
| Ordinance No. 3 of 27/07/1998 on the functions and the tasks of the officials of the specialized services in the enterprises for organization of the implementation of the activities related to protection against professional risks and prevention of such risks (title amended SG 102 of 22/12/2009, prom. SG 91 of 05/08/1998, as amended SG 102 of 22/12/2009) | Наредба № 3 от 27.07.1998 г. за функциите и задачите на длъжностните лица и на специализираните служби в предприятията за организиране изпълнението на дейностите, свързани със защитата от професионалните рискове и превенция на тези рискове (загл. изм. ДВ, бр. 102 от 22.12.2009 г., обн., ДВ, бр. 91 от 05.08.1998 г., изм., бр. 102 от 22.12.2009 г.) |
| Ordinance No. 15 of 31/05/1999 on the conditions, procedure and requirements to development and introduction of physiological regimes of labour and rest during work time (SG 54 of 15/06/1999) | Наредба № 15 от 31.05.1999 г. за условията, реда и изискванията за разработване и въвеждане на физиологични режими на труд и почивка по време на работа (обн., ДВ, бр. 54 от 15.06.1999 г.) |
| Ordinance No. 26 of 02/10/1996 on the rehabilitation of damaged terrains, improvement of low-productive lands, reclamation and recovery of humus layer (SG 89 of 22/10/1996, as amended and supplemented SG 30 of 22/03/2002) | Наредба № 26 от 02.10.1996 г. за рекултивация на нарушени терени, подобряване на слабопродуктивни земи, отнемане и оползотворяване на хумусния пласт (обн., ДВ, бр. 89 от 22.10.1996 г., изм. и доп. ДВ, бр. 30 от 22.03.2002 г.) |
| Ordinance on the categorization of the agricultural lands and the change of their purpose of use (adopted by CMD No. 261 of 17/10/1996, prom. SG 09 of 24/10/1996, as last amended SG 50 of 01/07/2011) | Наредба за категоризиране на земеделските земи при промяна на тяхното предназначение (приета с ПМС № 261 на МС от 17.10.1996 г., обн., ДВ, бр. 90 от 24.10.1996 г., посл. изм. ДВ, бр. 50 от 01.07.2011 г.); |
| Ordinance No. 1 of 10/03/1993 for protection of the terrains of greenery and decorative vegetation (SG 26 of 30/03/1993) | Наредба № 1 от 10.03.1993 г. за опазване на озеленените площи и декоративната растителност (обн., ДВ, бр. 26 от 30.03.1993 г.) |
| Ordinance No. 1 of 10/09/1996 for design of the flat foundation (SG 85 of 08/10/1996) | Наредба № 1 от 10.09.1996 г. за проектиране на плоско фундиране (обн., ДВ, бр. 85 от 08.10.1996 г.) |
| DECISIONS | РЕШЕНИЯ |
| Decision No. 122 of the Council of Ministers (CM) of 02/03/2007 for the adoption of a List of Protected Areas for Protection of Wild Birds and a List of Protected Areas for Protection of Natural Habitats and Wild Flora and Fauna (SG 21 of 09/03/3007, as last amended and supplemented SG 41 of 31/05/2011) | Решение № 122 на Министерски съвет (МС) от 02.03.2007 г. за приемане на Списък на защитените зони за опазване на дивите птици и на Списък на защитените зони за опазване на природните местообитания и на дивата флора и фауна (обн., ДВ, бр. 21 от 09.03.2007 г., посл. изм. и доп. ДВ, бр. 41 от 31.05.2011 г.) |
| Decision No. 661 of the CM of 16/10/2007 for the adoption of a List of Protected Areas for Protection of Natural Habitats and Wild Flora and Fauna (SG 85 of 23/10/3007, as last amended and supplemented SG 96 of 07/12/2010) | Решение № 661 на МС от 16.10.2007 г. за приемане на Списък на защитените зони за опазване на природните местообитания и на дивата флора и фауна (обн., ДВ, бр. 85 от 23.10.2007 г., посл. изм. и доп. ДВ, бр. 96 от 07.12.2010 г.) |
| Decision No. 802 of the CM of 04/12/2007 for the adoption of a List of Protected Areas for Protection of Wild Birds and a List of Protected Areas for Protection of Natural Habitats and Wild Flora and Fauna (SG 107 of 18/12/3007, as last amended and supplemented SG 41 of 31/05/2011) | Решение № 802 на МС от 04.12.2007 г. за приемане на Списък на защитени зони за опазване на дивите птици и на Списък на защитени зони за опазване на природните местообитания и на дивата флора и фауна (обн., ДВ, бр. 107 от 18.12.2007 г., посл. изм. и доп., ДВ, бр. 41 от 31.05.2011 г.) |
| INSTRUCTIONS AND ORDERS | ИНСТРУКЦИИ И ЗАПОВЕДИ |
| Order No. RD-272 of 03/05/2001 of the Minister of Environment and Water for categorization of surface waters in the water bodies or parts therein: http://www3.moew.government.bg/files/file/Water/Povarhnostnivodi/Zapovedi_PW/kategoriz_povarhn_vodi.pdf | Заповед № РД–272/03.05.2001 г. на Министъра на околната среда и водите за категоризацията на повърхностните води във водните обекти или в части от тях: http://www3.moew.government.bg/files/file/Water/Povarhnostnivodi/Zapovedi_PW/kategoriz_povarhn_vodi.pdf |
| Order No. RD-970 of 28/07/2003 of the Minister of Environment and Water for determination of the sensitive areas in the water bodies: http://www3.moew.government.bg/files/file/Water/OPVodi/Kanalizacionni_sistemi/Zapoved_za_opredeliane_na_chuvstvitelni_zoni.PDF | Заповед № РД-970/28.07.2003 г. на Министъра на околната среда и водите за определяне на чувствителните зони във водните обекти: http://www3.moew.government.bg/files/file/Water/OPVodi/Kanalizacionni_sistemi/Zapoved_za_opredeliane_na_chuvstvitelni_zoni.PDF |
| Order No. RD-821 of 30/10/2012 of the Minister of Environment and Water on the control activities on the permits entered in force: http://www3.moew.government.bg/files/file/Water/OPVodi/SOZ/Zapoved_RD-821_30.10.2012.pdf | Заповед № РД-821/30.10.2012 г. на Министъра на околната среда и водите за контролната дейност по влезли в сила разрешителни: http://www3.moew.government.bg/files/file/Water/OPVodi/SOZ/Zapoved_RD-821_30.10.2012.pdf |
| Order No. RD-918 of 10/12/2012 of the Minister of Environment and Water for annual submission of information to the MoEW and ExEA on the newly commissioned urban waste water treatment plants: http://www3.moew.government.bg/files/file/Water/OPVodi/Kanalizacionni_sistemi/RD-918_10.12.2012.pdf | Заповед № РД-918/10.12.2012 г. на Министъра на околната среда и водите за ежегодно изпращане в МОСВ и в ИАОС на информация за нововъведени в експлоатация селищни пречиствателни станции за отпадъчни води: http://www3.moew.government.bg/files/file/Water/OPVodi/Kanalizacionni_sistemi/RD-918_10.12.2012.pdf |
| Order No. RD-09-616 of 21/07/2010 on the adoption of the Conditions for Maintenance of Land in Good Agricultural and Ecological Status: http://www.mzh.government.bg/mzh/ShortLinks/DZEU/NacionalniStandarti.aspx | Заповед № РД 09-616 от 21.07.2010 г. за одобряване на Условия за поддържане на земята в добро земеделско и екологично състояние: http://www.mzh.government.bg/mzh/ShortLinks/DZEU/NacionalniStandarti.aspx |
| Instruction on the determination of the type and the level of pollution of agricultural lands in for each territory and the regime for their use, approved by Order No. RD-00-11/1994 of the Ministry of Agriculture (MA)published in the Information Bulletin No. 27 of the MA, Sofia, 1994 | Инструкция за определяне на вида и степента на замърсяването на земеделските земи по землища и режима на тяхното ползване. Информационен бюлетин № 27 на МЗ. София, 1994 (№ РД-00-11 на Министерство на земеделието); |
| Norms for design of sewage systems, adopted by Order No. RD-02-14-140 of 17/04/1989, published in Bulletin for Construction and Architecture (BCA), book 9 and 10, as amended BCA, book 1 of 1993, ISBN: 9548873569 | Норми за проектиране на канализационни системи, приети със заповед № РД-02-14-140 от 17.04.1989 г., публ., Бюлетин за строителство и архитектура (БСА), кн. 9 и 10 от 1989 г., изм., БСА, кн. 1 от 1993 г.: |

REMARK: The list above was last updated on 15/04/2013 and it does not aim to be exhaustive.

ANNEX 3

List of judgements of the court of justice of the EU most relevant to the guidelines

- Judgement on Case C-396/00 (Commission v. Italy): not ensuring that by 31 December 1998 at the latest the discharges of urban waste water of the city of Milan, located within a catchment area draining into areas of the delta of the River Po and the north-west coast of the Adriatic Sea defined by Decree-Law and implementing Directive 91/271/EEC and Directive 91/676/EEC as sensitive, within the meaning of Article 5 of Council Directive 91/271/EEC of 21 May 1991 concerning urban waste-water treatment (OJ 1991 L 135, p. 40), were subjected to more stringent treatment than secondary treatment or an equivalent treatment prescribed by Article 4 of that directive;

- Judgement on Case C-419/01 (Commission v. Spain): failure to identify sensitive areas in only some regions of its territory, under Article 5 of Council Directive 91/271/EEC;

- Judgement on Case C-119/02 (Commission v. Greece): failure takе the measures necessary for the installation of a collecting system for urban waste water from the area of Thriasio Pedio and not subjecting urban waste water from that area to treatment more stringent than secondary treatment before its discharge into the sensitive area of the Gulf of Elefsina under Articles 3(1) and 5(2) of Council Directive 91/271/EEC;

- Judgement on Case C-280/02 (Commission v. France): failure to identify certain areas as sensitive to eutrophication as regards the Seine-Normandy basin, Loire-Bretagne, Artois-Picardie and Rhône-Méditerranée-Corse and to submit to more stringent treatment discharges of urban waste water from agglomerations with a population equivalent of more than 10,000 in sensitive areas or who have been identified as sensitive;

- Judgement on Case C-27/03 (Commission v. Belgium): failure to adopt the laws, regulations and administrative provisions necessary to the full implementation of Articles 3, 5 and 17 - the latter in conjunction with Articles 3 and 4 - Directive 91/271/EEC and the Commission decision 93/481/EEC;

- Judgement on Case C-332/04 (Commission v. Spain): incomplete/incorrect transposition of Arts 3, 9(1) and Paragraph 10(b) of Annex II to Council Directive 85/337/EEC; failure to apply the transitional scheme established by Article 3 of Directive 97/11/EC; failure to have submitted a construction project for a leisure complex at Paterna (Valencia) for an assessment;

- Judgement on Case C-219/05 (Commission v. Spain): failure to subject urban waste water from the agglomeration of Sueca, the coastal districts of the latter (El Perello, The Palmeres Mareny of Barrequetes, Playa del Rey and Boga de Mar) and certain municipalities in the region La Ribera (Benifaió, Sollana and Almussafes) to appropriate treatment before being discharged into an area identified as sensitive (under Articles 3, 4 and 5, paragraph 2, of Council Directive 91/271/EEC);

- Judgement on Case C-252/05 (Thames Water Utilities Ltd): waste: directives 75/442/EEC, 91/156/EEC and 91/271/EEC; waste water which escapes from a sewerage network; classification; scope of directives 75/442/EEC and 91/271/EEC;

- Judgement on Case C-293/05 (Commission v. Italy): failure to takе the measures to ensure that by 31 December 1998 urban waste water from the agglomeration formed by several municipalities in the province of Varese are subject to more stringent treatment than secondary treatment or equivalent provided for in Article 4 of Council Directive 91/271/EEC (under Article 5, paragraphs 2 and 5 of the Directive);

- Judgement on Case C-405/05 (Commission v. UK): failure of a Member State to fulfil obligations – Directive 91/271/EEC; pollution and nuisance; lack of measures to ensure the adequate treatment of urban waste water from a number of agglomerations);

- Judgement on Case C-452/05 (Commission v. Grand-Duché de Luxembourg): declaration that, by not being able to prove that the minimum percentage of reduction of the overall load entering all treatment plants is at least 75% for total phosphorus and at least 75% for total nitrogen (Article 5, paragraph 4, of the Council Directive 91/271/EEC);

- Judgement on Case C-316/06 (Commission v. Ireland): declaration that, by not ensuring, firstly, that urban waste water agglomerations referred IE22, Bray, IE31, Howth, IE34, Letterkenny, IE40, Shanganagh, IE41, Sligo, and IE45, Tramore County Waterford, entering collection systems shall before discharge be subject to secondary treatment or an equivalent treatment, the deadline of 31 December 2000 at the latest, and, secondly, that the said water discharges meet later than the above deadline, the requirements of Annex I, point B of Council Directive 91/271/EEC;

- Judgement on Case C-440/06 (Commission v. Greece): failure of a MS to fulfil obligations; breach of Articles 3 and 4 of Council Directive 91/271/EEC of 21 May 1991; failure to have ensured appropriate treatment of urban waste water in 24 agglomerations;

- Judgement on Case C-335/07 (Commission v. Sweden): failure of a MS to fulfil obligations; Directive 91/271/EEC; treatment of urban waste water; failure to require more stringent treatment of nitrogen in all treatment plants of urban waste water from agglomerations of more than 10 000 р.е.;

- Judgement on Case C-390/07 (Commission v. UK): declaration that, by having failed to identify the Humber Estuary, the Wash, the Deben and Colne Estuaries, the Outer Thames Estuary, Southampton Water and the North East Irish Sea – with the exception of the Solway Firth – as sensitive areas with respect to eutrophication and by having failed to subject to more stringent treatment discharges of urban waste water from agglomerations with a population equivalent (p.e.) of more than 10 000 into the Humber Estuary, the Wash, the Deben and Colne Estuaries, the Outer Thames Estuary, Southampton Water and the North East Irish Sea – with the exception of the Solway Firth – and into Lough Neagh and Upper and Lower Lough Erne, the United Kingdom of Great Britain and Northern Ireland has failed to fulfil its obligations pursuant to Articles 3(1) and (2) and 5(1) to (3) and (5) of, and Annex II to, Council Directive 91/271/EEC;

- Judgement on Case C-438/07 (Commission v. Sweden): failure of a Member State to fulfil obligations; Directive 91/271/EEC treatment of urban waste water; failure to require more stringent treatment of nitrogen in all treatment plants of urban waste water from agglomerations of more than 10 000 р.е.;

- Judgement on Case C-571/11 (Commission v. Greece): failure to takе the necessary steps to avoid the deterioration of natural habitats and habitats of species for which the Special Protection Area and ranked by not being a system of collection and treatment of urban waste water for the city of Langadas (obligations under Article 6, paragraph 2 of Directive 92/43/EEC in conjunction with Article 7 of this Directive and under Articles 3 and 4, paragraphs 1 and 3 of Council Directive 91/271/EEC).

REMARK: The list above is not exhaustive, but provides a reference to some judgments of the CJEU, which should be borne in mind when EIA for waste water projects is carried out. It should be noted that the users of this Guidelines should check regularly for new relevant case-law of the Court.

# Footnotes

As defined by Ordinance No. 6 of 09/11/2000 on the emission values of admissible content of harmful and dangerous substances in waste waters discharged in water bodies (SG 97 of 28/11/2000 as amended and supplemented SG 24 of 23/03/2004)

Namely projects to which the terms ‘urban’ and ‘infrastructure’ can relate, such as the construction of sewerage and water supply networks “Interpretation of definitions of certain project categories of annex I and II of the EIA Directive”, prepared by the Environment Directorate-General of the European Commission

In some cases EU Member States have also negotiated transitional periods for application of Directive 91/271/EEC which also need to be considered.

Source: Процедурата за издаване на  строителни разрешителни: подобрена и в интернет (available only in Bulgarian): http://ime.bg/uploads/38bea8_Kiniga_edit.pdf

National Environmental Protection Strategy 2000-2006: http://www.moew.government.bg/?show=19

National Action Programme for Environment and Health 2008-2013: http://www.moew.government.bg/?show=19

Pursuant to the LEP, the term ‘project’ under Article 1(2)(a) of the EIAD in Bulgarian national legislation is referred to as ‘investment proposal’.

For reference: Interpretation of definitions of certain project categories of Annex I and II of the EIA Directive: http://ec.europa.eu/environment/eia/pdf/interpretation_eia.pdf

For reference: Interpretation of definitions of certain project categories of Annex I and II of the EIA Directive: http://ec.europa.eu/environment/eia/pdf/interpretation_eia.pdf

For reference: Judgements on cases C-392/96, Commission v. Ireland, paragraphs, 76, 82; C-142/07, Ecologistas en Acción-CODA, paragraph 44 and C-205/08, Umweltanwalt von Kärnten, paragraph 53

Pursuant to the LBD, the ‘appropriate assessment’ under Article 6(3) of the HD in Bulgarian national legislation is referred to as ‘compatibility assessment’.

Source: MOCB, Доклад към 31.12.2010 г. за прилагане на Директива 91/271/ЕЕС относно пречистване на отпадъчни води от населените места – предназначен за обществеността

Point 10(c) of Annex VI: List referred to in Article 20 of the Protocol: transitional measures, Bulgaria under the Accession Treaty

Article 11(2) „The waste waters from agglomerations discharged into water sites located in mountain areas over 1500 m over sea level, can be subject to more simplified treatment from this in para 1 if detailed investigations show, that these discharges do not render unfavourable influence on the environment.“

"1 p.e. (population equivalent)" means organic biodegradable load having a five-day biochemical oxygen demand (BOD5) of 60 g of oxygen per day (Article 2(6) of Council Directive 91/271/EEC concerning urban waste-water treatment), respectively, point 8 of the Additional Provisions to Ordinance No. 6 of 9 November 2000 on the emission values of admissible content of harmful and dangerous substances in waste waters discharged in water bodies “"1 p.e. (population equivalent)” means the organic biodegradable load having a five-day biochemical oxygen demand (BOD5) of 60 g of oxygen per day”

"Sludge" means residual sludge, whether treated or untreated, from urban waste water treatment plants (Council Directive 91/271/EEC concerning urban waste-water treatment), respectively as defined by point 34 of the Additional Provisions to Ordinance No. 6 of 09/11/2000 on the emission values of admissible content of harmful and dangerous substances in waste waters discharged in water bodies: “"sludge from urban waste water treatment plants" means residual sludge from such plants, whether treated or untreated;”

European Waste established by Commission decision 2000/532/EC (amended by Decisions 2001/118/EC, 2001/119/EC and 2001/216/EC), as transposed by Ordinance 3 of 01/04/2004 on the classification of waste

According to the Habitats Directive 92/43/EEC, respectively the CA under the LBD and the CA Ordinance.

Note that these effects or impacts will have to be described in terms of their character and duration, e.g. permanent, temporary, short, medium or long-term; continuous, intermittent, or occasional; reversible or irreversible

EIAD, Annex IV, respectively Article 96 of the LEP

Anticipation of future loads will take into consideration the areas development ( from urban development point of view) and predictions of the possible changes of industrial discharges (reduction or increase of flows and specific pollutants)

"Appropriate treatment" means treatment of urban waste water by any process and/or disposal system which after discharge allows the receiving waters to meet the relevant quality objectives and the relevant provisions of this and other Community Directives – Article 2(9) of Directive 91/271/EEC of 21 May 1991 concerning urban waste water treatment. This definition is transposed in point 26 of the Additional Provisions to Ordinance No. 6 of 09/11/2000 on the emission values of admissible content of harmful and dangerous substances in waste waters discharged in water bodies (SG 97 of 28/11/2000 as amended and supplemented SG 24 of 23/03/2004) is the following way: “"appropriate  treatment" means treatment of waste waters from the settlements in such a way, which after their discharge ensures the observing of the imission standards of the water intake and the observing of the provisions of this ordinance”.

If it is known at the stage of EMP elaboration.